## NSW.buses
The data included below reflects information available as of 8 March 2011.
More up-to-date information may be found: |  |  |  | http://www.moxy.com.au/Wiki/index.php/NSW_Electricity_Network
The NSW Electricity Network is made up of the following buses.
Bus | Id | RealPowerDemand | ReactivPowerDemand | ShuntSusceptance | VoltageMagnitude | RealPowerOutput | MaximumReactivePowerOutput | MinimumReactivePowerOutput | VoltageMagnitudeSetpoint
Armidale Electrical Bus | 2 | 230 MW | 10 MVA | -0.623 MVA
Avon Electrical Bus | 29 | 0 MW | 0 MVA | 0 MVA
Bayswater Powerstation | 9 | 0 MW | 0 MVA | 0 MVA | 1.057 | 0 MW | 0 MVA | 0 MVA | 1.057
Beaconsfield West Electrical Bus | 27 | 590 MW | 170 MVA | 0 MVA
Canberra Electrical Bus | 33 | 0 MW | 0 MVA |  | 1 | 230 MW | 0 MVA | 0 MVA | 1
Dapto Electrical Bus | 28 | 460 MW | 40 MVA | 0 MVA
Dederang Electrical Bus | 40 | 940 MW | -350 MVA | 0 MVA
Dumaresq Substation | 1 | 0 MW | 0 MVA |  | 1.035 | 1000 MW | 0 MVA
Eraring Powerstation | 10 | 190 MW | -142 MVA |  | 1.03 | 1200 MW | 0 MVA | 0 MVA | 1.03
Ingleburn Electrical Bus | 23 | 113 MW | 71 MVA | 0 MVA
Jindera Electrical Bus | 38 | 122 MW | 86 MVA | 0 MVA
Kangaroo Valley Electrical Bus | 32 | 521 MW | 270 MVA | 0 MVA
Kemps Creek Electrical Bus | 11 | 0 MW | 0 MVA |  | 1 | 1390 MW | 0 MVA | 0 MVA | 1
Liddell Powerstation | 6 | 40 MW | 90 MVA |  | 1.05 | 1850 MW | 0 MVA | 0 MVA | 1.05
Lismore Electrical Bus | 3 | 140 MW | 36 MVA | -0.044 MVA
Liverpool Electrical Bus | 24 | 240 MW | 38 MVA | 0 MVA
Lower Tumut Electrical Bus | 34 | 2 MW | -300 MVA | 0 MVA
Marulan Electrical Bus | 30 | 82 MW | 20 MVA | 0 MVA
Mount Piper Powerstation | 20 | 120 MW | 16 MVA |  | 1.03 | 570 MW | 0 MVA | 0 MVA | 1.03
Munmorah Powerstation | 13 | 21 MW | 46 MVA |  | 1.02 | 470 MW | 0 MVA | 0 MVA | 1.02
Murray Electrical Bus | 35 | 0 MW | -13.5 MVA | 0 MVA
Muswellbrook Electrical Bus | 5 | 20 MW | 120 MVA | 0 MVA
Newcastle Electrical Bus | 7 | 1000 MW | 290 MVA | 0 MVA
Regentville Electrical Bus | 19 | 150 MW | 90 MVA | 0 MVA
Sterland Electrical Bus | 14 | 0 MW | 0 MVA | 1
Sydney East Electrical Bus | 17 | 570 MW | 50 MVA | 0 MVA
Sydney North Electrical Bus | 16 | 1070 MW | -226 MVA | 0 MVA
Sydney South Electrical Bus | 26 | 903 MW | -61 MVA | 0 MVA
Sydney West Electrical Bus | 18 | 1070 MW | 210 MVA | 0 MVA
Tamworth Electrical Bus | 4 | 130 MW | 17 MVA | 0.817 MVA
Tomago Aluminium Smelter | 8 | 740 MW | 280 MVA | 1.37 MVA
Tuggerah Electrical Bus | 15 | 230 MW | 80 MVA | 0 MVA
Upper Tumut Electrical Bus | 36 | 0 MW | -14.4 MVA | 0 MVA
Vales Point Powerstation | 12 | 33 MW | 17 MVA |  | 1.02 | 1200 MW | 0 MVA | 0 MVA | 1.02
Vineyard Electrical Bus | 25 | 103 MW | 69 MVA | 0 MVA
Wagga Wagga Electrical Bus | 37 | 250 MW | -131.7 MVA | 0 MVA
Wallerawang Powerstation | 22 | 150 MW | 18 MVA |  | 1.03 | 890 MW | 0 MVA | 0 MVA | 1.03
Wellington Electrical Bus | 21 | 200 MW | 35 MVA | 0 MVA
Wodonga Electrical Bus | 39 | 40 MW | 36 MVA | 0 MVA
Yass Electrical Bus | 31 | 216 MW | 16 MVA | 0 MVA

## NSW.Transmission
The data included below reflects information available as of 8 March 2011.
More up-to-date information may be found: |  |  |  | http://www.moxy.com.au/Wiki/index.php/NSW_Electricity_Network
The NSW Electricity Network is made up of the following transmission lines.
Line | ShortName | FromBus | FromId | ToBus | ToId | Resistance | Reactance | TotalLineChargingSusceptance
01X Electrical Transmission Line | '01X' | Kangaroo Valley Electrical Bus | 32 | Yass Electrical Bus | 31 | 0.001692 | 0.01301 | 0.1595
01 Electrical Transmission Line | '01' | Kangaroo Valley Electrical Bus | 32 | Upper Tumut Electrical Bus | 36 | 0.003818 | 0.03245 | 0.3617
02 Electrical Transmission Line | '02' | Yass Electrical Bus | 31 | Upper Tumut Electrical Bus | 36 | 0.005888 | 0.04686 | 0.5542
03 Electrical Transmission Line | '03' | Yass Electrical Bus | 31 | Lower Tumut Electrical Bus | 34 | 0.005166 | 0.03951 | 0.4901
051 Electrical Transmission Line | '051' | Lower Tumut Electrical Bus | 34 | Wagga Wagga Electrical Bus | 37 | 0.004022 | 0.03071 | 0.3822
07 Electrical Transmission Line | '07' | Kangaroo Valley Electrical Bus | 32 | Lower Tumut Electrical Bus | 34 | 0.003972 | 0.03046 | 0.3735
10 Electrical Transmission Line | '10' | Avon Electrical Bus | 29 | Dapto Electrical Bus | 28 | 0.000311 | 0.003298 | 0.04159
11 Electrical Transmission Line | '11' | Sydney South Electrical Bus | 26 | Dapto Electrical Bus | 28 | 0.00195 | 0.02061 | 0.2602
12 Electrical Transmission Line | '12' | Liverpool Electrical Bus | 24 | Sydney South Electrical Bus | 26 | 0.000522 | 0.005267 | 0.07325
13 Electrical Transmission Line | '13' | Kemps Creek Electrical Bus | 11 | Sydney South Electrical Bus | 26 | 0.00069 | 0.006991 | 0.09616
14 Electrical Transmission Line | '14' | Sydney North Electrical Bus | 16 | Kemps Creek Electrical Bus | 11 | 0.001431 | 0.01504 | 0.1914
16 Electrical Transmission Line | '16' | Avon Electrical Bus | 29 | Marulan Electrical Bus | 30 | 0.002838 | 0.02178 | 0.2673
18 Electrical Transmission Line | '18' | Canberra Electrical Bus | 33 | Dapto Electrical Bus | 28 | 0.001713 | 0.01317 | 0.1615
20 Electrical Transmission Line | '20' | Sydney North Electrical Bus | 16 | Sydney West Electrical Bus | 18 | 0.000954 | 0.01007 | 0.1273
21A Electrical Transmission Line | '21A' | Munmorah Powerstation | 13 | Sterland Electrical Bus | 14 | 0.000759 | 0.008023 | 0.1012
21B Electrical Transmission Line | '21B' | Sterland Electrical Bus | 14 | Tuggerah Electrical Bus | 15 | 0.000398 | 0.004073 | 0.05128
21C Electrical Transmission Line | '21C' | Sterland Electrical Bus | 14 | Sydney North Electrical Bus | 16 | 0.001462 | 0.01549 | 0.1954
22 Electrical Transmission Line | '22' | Vales Point Powerstation | 12 | Sydney North Electrical Bus | 16 | 0.002463 | 0.02611 | 0.3292
23 Electrical Transmission Line | '23' | Vales Point Powerstation | 12 | Munmorah Powerstation | 13 | 0.000208 | 0.002174 | 0.0274
24 Electrical Transmission Line | '24' | Newcastle Electrical Bus | 7 | Vales Point Powerstation | 12 | 0.00106 | 0.01013 | 0.148
25 Electrical Transmission Line | '25' | Eraring Powerstation | 10 | Vineyard Electrical Bus | 25 | 0.003147 | 0.03074 | 0.4496
26 Electrical Transmission Line | '26' | Munmorah Powerstation | 13 | Sydney West Electrical Bus | 18 | 0.003555 | 0.035 | 0.5077
27 Electrical Transmission Line | '27' | Sydney North Electrical Bus | 16 | Sydney East Electrical Bus | 17 | 0.000631 | 0.006431 | 0.08611
28 Electrical Transmission Line | '28' | Sydney North Electrical Bus | 16 | Sydney East Electrical Bus | 17 | 0.000647 | 0.006769 | 0.08545
29 Electrical Transmission Line | '29' | Sydney West Electrical Bus | 18 | Vineyard Electrical Bus | 25 | 0.000591 | 0.005796 | 0.08479
30 Electrical Transmission Line | '30' | Sydney West Electrical Bus | 18 | Liverpool Electrical Bus | 24 | 0.00048 | 0.005035 | 0.06366
31 Electrical Transmission Line | '31' | Bayswater Powerstation | 9 | Regentville Electrical Bus | 19 | 0.004892 | 0.04799 | 0.7021
32 Electrical Transmission Line | '32' | Bayswater Powerstation | 9 | Sydney West Electrical Bus | 18 | 0.00541 | 0.05293 | 0.7742
33 Electrical Transmission Line | '33' | Liddell Powerstation | 6 | Bayswater Powerstation | 9 | 0.000176 | 0.001696 | 0.02482
34 Electrical Transmission Line | '34' | Liddell Powerstation | 6 | Bayswater Powerstation | 9 | 0.000176 | 0.001696 | 0.02482
35 Electrical Transmission Line | '35' | Mount Piper Powerstation | 20 | Marulan Electrical Bus | 30 | 0.002841 | 0.0375 | 0.8098
36 Electrical Transmission Line | '36' | Mount Piper Powerstation | 20 | Marulan Electrical Bus | 30 | 0.00284 | 0.0375 | 0.8097
37 Electrical Transmission Line | '37' | Avon Electrical Bus | 29 | Kemps Creek Electrical Bus | 11 | 0.001821 | 0.01929 | 0.2521
38 Electrical Transmission Line | '38' | Sydney West Electrical Bus | 18 | Regentville Electrical Bus | 19 | 0.000501 | 0.004912 | 0.07186
39 Electrical Transmission Line | '39' | Sydney West Electrical Bus | 18 | Yass Electrical Bus | 31 | 0.009566 | 0.07349 | 0.9011
41 Electrical Transmission Line | '41' | Sydney South Electrical Bus | 26 | Beaconsfield West Electrical Bus | 27 | 0.000396 | 0.003412 | 2.479
4 Electrical Transmission Line | '4' | Marulan Electrical Bus | 30 | Yass Electrical Bus | 31 | 0.00458 | 0.0351 | 0.4311
5 Electrical Transmission Line | '5' | Marulan Electrical Bus | 30 | Yass Electrical Bus | 31 | 0.004735 | 0.03642 | 0.4465
62 Electrical Transmission Line | '62' | Wagga Wagga Electrical Bus | 37 | Jindera Electrical Bus | 38 | 0.003996 | 0.03084 | 0.3756
64 Electrical Transmission Line | '64' | Lower Tumut Electrical Bus | 34 | Upper Tumut Electrical Bus | 36 | 0.001607 | 0.01295 | 0.1508
65 Electrical Transmission Line | '65' | Murray Electrical Bus | 35 | Upper Tumut Electrical Bus | 36 | 0.001797 | 0.01464 | 0.1679
66 Electrical Transmission Line | '66' | Lower Tumut Electrical Bus | 34 | Murray Electrical Bus | 35 | 0.00298 | 0.0263 | 0.2778
67 Electrical Transmission Line | '67' | Murray Electrical Bus | 35 | Dederang Electrical Bus | 40 | 0.00441 | 0.0343 | 0.451
68 Electrical Transmission Line | '68' | Murray Electrical Bus | 35 | Dederang Electrical Bus | 40 | 0.00438 | 0.0342 | 0.45
6 Electrical Transmission Line | '6' | Canberra Electrical Bus | 33 | Kangaroo Valley Electrical Bus | 32 | 0.007606 | 0.05851 | 0.7172
71 Electrical Transmission Line | '71' | Mount Piper Powerstation | 20 | Wallerawang Powerstation | 22 | 0.000232 | 0.002224 | 0.03231
72 Electrical Transmission Line | '72' | Mount Piper Powerstation | 20 | Wellington Electrical Bus | 21 | 0.006822 | 0.05214 | 0.6582
73 Electrical Transmission Line | '73' | Bayswater Powerstation | 9 | Mount Piper Powerstation | 20 | 0.003977 | 0.05241 | 1.131
74 Electrical Transmission Line | '74' | Bayswater Powerstation | 9 | Wallerawang Powerstation | 22 | 0.004215 | 0.05465 | 1.164
76 Electrical Transmission Line | '76' | Sydney South Electrical Bus | 26 | Wallerawang Powerstation | 22 | 0.004063 | 0.03998 | 0.5879
77 Electrical Transmission Line | '77' | Wallerawang Powerstation | 22 | Ingleburn Electrical Bus | 23 | 0.003455 | 0.03408 | 0.4989
78 Electrical Transmission Line | '78' | Sydney South Electrical Bus | 26 | Ingleburn Electrical Bus | 23 | 0.0006 | 0.005834 | 0.08791
81 Electrical Transmission Line | '81' | Liddell Powerstation | 6 | Newcastle Electrical Bus | 7 | 0.002914 | 0.03058 | 0.3856
82 Electrical Transmission Line | '82' | Liddell Powerstation | 6 | Tomago Aluminium Smelter | 8 | 0.003321 | 0.03439 | 0.4456
83 Electrical Transmission Line | '83' | Muswellbrook Electrical Bus | 5 | Liddell Powerstation | 6 | 0.000704 | 0.005355 | 0.06807
84 Electrical Transmission Line | '84' | Tamworth Electrical Bus | 4 | Liddell Powerstation | 6 | 0.005571 | 0.04298 | 0.5282
85 Electrical Transmission Line | '85' | Armidale Electrical Bus | 2 | Tamworth Electrical Bus | 4 | 0.005511 | 0.03368 | 0.4255
86 Electrical Transmission Line | '86' | Armidale Electrical Bus | 2 | Tamworth Electrical Bus | 4 | 0.004159 | 0.03198 | 0.3921
88 Electrical Transmission Line | '88' | Tamworth Electrical Bus | 4 | Muswellbrook Electrical Bus | 5 | 0.005086 | 0.03913 | 0.4798
89 Electrical Transmission Line | '89' | Armidale Electrical Bus | 2 | Lismore Electrical Bus | 3 | 0.01222 | 0.09428 | 1.149
8C Electrical Transmission Line | '8C' | Dumaresq Substation | 1 | Armidale Electrical Bus | 2 | 0.003762 | 0.04763 | 0.7243
8E Electrical Transmission Line | '8E' | Dumaresq Substation | 1 | Armidale Electrical Bus | 2 | 0.003798 | 0.04755 | 0.7243
8 Electrical Transmission Line | '8' | Marulan Electrical Bus | 30 | Dapto Electrical Bus | 28 | 0.002849 | 0.02182 | 0.2681
92 Electrical Transmission Line | '92' | Newcastle Electrical Bus | 7 | Vales Point Powerstation | 12 | 0.001345 | 0.01389 | 0.1797
93 Electrical Transmission Line | '93' | Newcastle Electrical Bus | 7 | Eraring Powerstation | 10 | 0.000608 | 0.005983 | 0.08332
94 Electrical Transmission Line | '94' | Newcastle Electrical Bus | 7 | Tomago Aluminium Smelter | 8 | 0.000717 | 0.006888 | 0.0993
99B Electrical Transmission Line | '99B' | Jindera Electrical Bus | 38 | Wodonga Electrical Bus | 39 | 0.00164 | 0.01259 | 0.1646
99X Electrical Transmission Line | '99X' | Wodonga Electrical Bus | 39 | Dederang Electrical Bus | 40 | 0.0016 | 0.0123 | 0.16226