## BuildingSummary
Building Summary Outpatient Health Care pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care Reference Building pre-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 3804.01 | Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health Care Facilities – 30% Energy Savings. Golden, CO: National Renewable Energy Laboratory, NREL/TP-550-46314. Available at www.nrel.gov/docs/fy10osti/46314.pdf
| Building Shape | Irregular
| Aspect Ratio | 1.43
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.2408
| East | 0.1914
| North | 0.2052
| West | 0.1288
| Total | 0.1985
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Zoned By Use
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | Doebber, et al. 2009
Fabric
Exterior walls
| Construction Type | Steel frame | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1553.34
| Net Dimensions - Total Area (m2) | 1245.05
| Wall to Skin Ratio | 0.53076
Roof
| Construction Type | IEAD | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1373.29
| Net Dimensions - Total Area (m2) | 1373.29
| Roof to Skin Ratio | 0.46924
Window Dimensions (m2)
| South | 114.08
| East | 57.97
| North | 97.22
| West | 39.02
| Total Area (m2) | 308.29
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor | Doebber, et al. 2009
| Construction | 8in slab w/carpet | Doebber, et al. 2009
| Dimensions - Total Area (m2) | 1373.29
Interior Partitions
| Construction | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 2746.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ft3/min per ft2 of exterior wall) | 0.93401
HVAC
| System Type | Packaged VAV With Reheat | Doebber, et al. 2009
| Heating Type | Hot Water Boiler, Furnace | Doebber, et al. 2009
| Cooling Type | DX Cooling Coil | Doebber, et al. 2009
| Fan Control | VAV | Doebber, et al. 2009
Service Water Heating
| SWH Type | Gas Water Heater
| Fuel | Gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 240.48

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 22.6042 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 1.1157
Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0
Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 13.9931 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.63761
Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 13.9931 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0
Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 13.9931 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0
Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 19.375 | 11.84 |  |  | 10 |  | 5.8529 |  | 0
Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 19.375 | 11.84 |  |  | 10 |  | 2.0903 |  | 2.6777
Floor 1 Electrical Room | No | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 7.5347 | 53.82 | [6 empty] | 0.95598
Floor 1 Elevator Pump Room | No | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 7.5347 | 529.29 | [6 empty] | 2.9428
Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 19.375 | 11.84 |  |  | 10 |  | 2.5084 |  | 0
Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0
Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 19.375 | 11.84 |  |  | 10 |  | 5.2026 |  | 0
Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 10.7639 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.47364
Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0
Floor 1 Lobby Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 9.6875 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.44637
Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 9.6875 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0
Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 4.9269
Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 22.6042 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.39894
Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0
Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 22.6042 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0
Floor 1 MRI Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 22.6042 | 21.53 |  |  | 10 |  | 33.8167 |  | 0
Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Nurse Janitor | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 22.6042 | 21.53 |  |  | 10 |  | 48.4954 |  | 0
Floor 1 Nurse Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 0
Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 19.375 | 11.84 |  |  | 10 |  | 22.4361 |  | 0
Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 1.2518
Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.66961
Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0
Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 24.757 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0
Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0
Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 15.0695 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.28369
Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 15.0695 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0
Floor 1 Pre-Op Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 1.4867
Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 17.2222 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.89261
Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 10.7639 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.34207
Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0
Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 24.757 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 1.116
Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 19.375 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.78728
Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0
Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 9.6875 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0
Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 9.6875 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0
Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 9.6875 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0
Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 24.757 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 1.6513
Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.17385
Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0
Floor 1 Storage | No | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 10.7639 | 0 | [6 empty] | 2.256
Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.95671
Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.83664
Floor 1 Utility Janitor | No | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 1 Utility Room | No | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 2.0084
Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 1.4874
Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 19.375 | 10.76 |  |  | 10 |  | 156.0771 |  | 1.594
Floor 2 Conference Toilet | No | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 50.3426 | 0
Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 19.375 | 11.84 |  |  | 10 |  | 3.2516 |  | 0
Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 17.2222 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 1.5622
Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 17.2222 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.44628
Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 17.2222 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.44641
Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 17.2222 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 1.1153
Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 17.2222 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.95663
Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 17.2222 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.89298
Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 17.2222 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.40583
Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 17.2222 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.89255
Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 17.2222 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.40583
Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 3.3997
Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 9.6875 | 32.29 |  |  | 8 |  | 8.9187 |  | 0
Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 22.6042 | 21.53 |  |  | 10 |  | 27.8709 |  | 0
Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 22.6042 | 21.53 |  |  | 10 |  | 33.4451 |  | 0
Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 19.375 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.95642
Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0
Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 10.7639 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.66676
Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 2.2318
Floor 2 Reception Toilet | No | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 99.1089 | 0
Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 19.375 | 11.84 |  |  | 10 |  | 15.0503 |  | 0
Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 19.375 | 11.84 |  |  | 10 |  | 15.8864 |  | 0
Floor 2 Storage 1 | No | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Storage 2 | No | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Storage 3 | No | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 0
Floor 2 Utility | No | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 10.7639 | 1.08 | [6 empty] | 0.95631
Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 19.375 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.20596
Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.096261
Floor 2 Work Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 22.6042 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0
Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 19.375 | 11.84 |  |  | 10 |  | 1.951 |  | 1.339
Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 1.4839
Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 19.375 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 1.339
Floor 3 Janitor | No | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 4.7387
Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 9.6875 | 32.29 |  |  | 8 |  | 13.378 |  | 1.339
Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 9.6875 | 32.29 |  |  | 8 |  | 84.6161 |  | 1.7448
Floor 3 Lounge Toilet | No | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 8.6111 | 4.31 | [5 empty] | 151.023 | 2.1761
Floor 3 Mechanical | No | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 7.5347 | 53.82 | [6 empty] | 2.2957
Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 1.339
Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 19.375 | 11.84 |  |  | 10 |  | 141.0268 |  | 1.6654
Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 1.4353
Floor 3 Office Toilet | No | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 42.4752 | 2.8257
Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 2.2146
Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 1.339
Floor 3 Physical Therapy Toilet | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 | [5 empty] | 66.0726 | 1.339
Floor 3 Storage 1 | No | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
Floor 3 Storage 2 | No | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 0 | [6 empty] | 1.339
Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 17.2222 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 1.339
Floor 3 Undeveloped 1 | No | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 |  | 0 | 0 | 0 | [6 empty] | 1.7641
Floor 3 Undeveloped 2 | No | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 |  | 0 | 0 | 0 | [6 empty] | 1.99
Floor 3 Utility | No | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 | [6 empty] | 1.339
Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 19.375 | 11.84 |  |  | 10 |  | 26.6632 |  | 2.2955
NE Stair | No | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 8.6111 | 0 | [6 empty] | 1
NW Elevator | No | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 8.6111 | 0 | [6 empty] | 1
NW Stair | No | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 8.6111 | 0 | [6 empty] | 1
SW Stair | No | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 8.6111 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 3088.5616 | 11932.163 |  | 1634.1215 | 308.28 |  | 398.9164
Data Source | [7 empty] | 1 |  | 2 | 5 | 5 | 5 | 3, 4 | 3, 4 | 3, 4 | 5 | 6
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health
[6] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Weighting Factor
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| AHU-1_COOLC DXCOIL | 280.9098 | 282.282 | 275.6667 | 272.8685 | 223.52 | 247.8325 | 202.8277 | 269.3367 | 236.622 | 209.6443 | 257.2825 | 221.6156 | 251.1956 | 213.3376 | 217.5178 | 186.287
| AHU-2_COOLC DXCOIL | 329.9329 | 343.6334 | 358.2695 | 331.5756 | 258.189 | 325.5341 | 236.9677 | 323.4525 | 268.7578 | 252.9276 | 297.4926 | 238.5169 | 282.4123 | 224.3634 | 243.4795 | 201.3402
Heating (kW)
| HEATSYS1 BOILER | 138.0095 | 138.3947 | 131.2853 | 140.2477 | 129.0934 | 128.3124 | 128.8264 | 143.9956 | 125.9352 | 134.3732 | 148.0501 | 130.6299 | 154.1922 | 144.5644 | 152.2497 | 173.9062
HVAC Efficiency
Air Conditioning (COP)
| AHU-1_COOLC DXCOIL | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.11 | 3.01 | 3.01 | 3.11 | 3.01 | 3.11 | 3.01 | 3.11 | 3.11 | 3.11
| AHU-2_COOLC DXCOIL | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.01 | 3.11
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74 | 0.74
HVAC Control - Economizer
| AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| AHU-1_FAN | 12.91 | 13.07 | 13.49 | 13.44 | 12.7 | 13.63 | 12.25 | 12.92 | 14.29 | 12.66 | 12.19 | 13.39 | 12.24 | 12.89 | 11.73 | 11.25
| AHU-2_FAN | 14.74 | 15.4 | 17.27 | 15.86 | 14.06 | 17.25 | 14.18 | 14.91 | 16.24 | 14.68 | 13.47 | 14.41 | 13.03 | 13.55 | 12.41 | 12.16
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.080254 | 0.10635 | 0.078191 | 0.098843 | 0.12314 | 0.091364 | 0.14403 | 0.068551 | 0.037037 | 0.071511 | 0.09697 | 0.037044 | 0.054177 | 0.071339 | 0.054073 | 0.090907
| Total Cost ($/m2) | 38.88 | 50.28 | 38.55 | 45.59 | 50.67 | 45.44 | 54.94 | 31.15 | 17.2 | 28.53 | 41.22 | 16.1 | 23.19 | 30.17 | 22.38 | 39.49
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011409 | 0.0081555 | 0.008585 | 0.010782 | 0.0083905 | 0.0081271 | 0.0083897 | 0.010099 | 0.0072206 | 0.0082733 | 0.0089745 | 0.0072283 | 0.0079809 | 0.0088442 | 0.00799 | 0.004192
| Total Cost ($/m2) | 8.35 | 7.14 | 7.89 | 10.9 | 8.42 | 7.42 | 8.81 | 10.67 | 6.75 | 9.19 | 9.35 | 6.67 | 8.76 | 8.99 | 8.84 | 5.65
Total Utility Costs
| Cost Intensity ($/m2) | 47.23 | 57.42 | 46.44 | 56.49 | 59.09 | 52.86 | 63.76 | 41.82 | 23.95 | 37.72 | 50.57 | 22.77 | 31.94 | 39.15 | 31.22 | 45.15
Energy - End Uses
Electricity (kWh)
| Heating | 10488.8889 | 51900 | 46827.7778 | 87505.5556 | 37244.4444 | 62791.6667 | 74513.8889 | 118747.2222 | 79363.8889 | 128650 | 116086.1111 | 84030.5556 | 130888.8889 | 111300 | 153500 | 235941.6667
| Cooling | 742988.8889 | 634663.8889 | 634947.2222 | 505519.4444 | 427300 | 527572.2222 | 296772.2222 | 423544.4444 | 371161.1111 | 270733.3333 | 316841.6667 | 279497.2222 | 282172.2222 | 225136.1111 | 186372.2222 | 129761.1111
| Interior Lighting | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667 | 221016.6667
| Exterior Lighting | 74091.6667 | 74063.8889 | 74050 | 74038.8889 | 73983.3333 | 73966.6667 | 74005.5556 | 73961.1111 | 73988.8889 | 73841.6667 | 73972.2222 | 73927.7778 | 73922.2222 | 73905.5556 | 73863.8889 | 73411.1111
| Interior Equipment | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778 | 499777.7778
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 287047.2222 | 288325 | 303288.8889 | 295030.5556 | 277175 | 306347.2222 | 266800 | 281633.3333 | 316463.8889 | 275352.7778 | 265072.2222 | 292452.7778 | 265647.2222 | 280030.5556 | 254558.3333 | 243722.2222
| Pumps | 6038.8889 | 6052.7778 | 5738.8889 | 6136.1111 | 5650 | 5583.3333 | 5638.8889 | 6272.2222 | 5513.8889 | 5875 | 6466.6667 | 5716.6667 | 6727.7778 | 6319.4444 | 6647.2222 | 7544.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 1536.1111 | 22725 | 89833.3333 | 65538.8889 | 22986.1111 | 194933.3333 | 12580.5556 | 103588.8889 | 199313.8889 | 42427.7778 | 117758.3333 | 196544.4444 | 147986.1111 | 191061.1111 | 178425 | 241405.5556
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1842983.3333 | 1798525 | 1875477.7778 | 1754561.1111 | 1565133.3333 | 1891986.1111 | 1451105.5556 | 1728538.8889 | 1766597.2222 | 1517675 | 1616988.8889 | 1652963.8889 | 1628138.8889 | 1608547.2222 | 1574163.8889 | 1652580.5556
Gas (MJ)
| Heating | 2568370 | 3106260 | 3277480 | 3619520 | 3592270 | 3252010 | 3765570 | 3789350 | 3326410 | 3991910 | 3728910 | 3277490 | 3935530 | 3626140 | 3966430 | 4880280
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 28110 | 33520 | 30380 | 38750 | 37740 | 34120 | 42220 | 42850 | 42060 | 44990 | 46480 | 46290 | 49570 | 50170 | 54750 | 60970
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2784850 | 3328150 | 3496230 | 3846650 | 3818390 | 3474510 | 3996160 | 4020580 | 3556840 | 4225280 | 3963760 | 3512150 | 4173480 | 3864680 | 4209550 | 5129630
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 9419590 | 9802840 | 10247960 | 10163070 | 9452870 | 10285660 | 9220140 | 10243310 | 9916590 | 9688910 | 9784930 | 9462820 | 10034780 | 9655450 | 9876540 | 11078930
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 9.9264 | 49.1166 | 44.3164 | 82.8126 | 35.247 | 59.4241 | 70.5177 | 112.3788 | 75.1076 | 121.7505 | 109.8604 | 79.524 | 123.8693 | 105.331 | 145.2678 | 223.2881
| Cooling (elec) | 703.1422 | 600.6267 | 600.8948 | 478.4083 | 404.3838 | 499.2784 | 280.8563 | 400.8297 | 351.2556 | 256.2138 | 299.8494 | 264.5077 | 267.0393 | 213.062 | 176.377 | 122.802
| Interior Lighting (elec) | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635 | 209.1635
| Exterior Lighting (elec) | 70.1181 | 70.0918 | 70.0787 | 70.0682 | 70.0156 | 69.9998 | 70.0366 | 69.9946 | 70.0208 | 69.8815 | 70.0051 | 69.963 | 69.9578 | 69.942 | 69.9026 | 69.4741
| Interior Equipment (elec) | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746 | 472.9746
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 271.6528 | 272.8621 | 287.0234 | 279.208 | 262.31 | 289.9177 | 252.4914 | 266.5293 | 299.4919 | 260.5855 | 250.8563 | 276.7685 | 251.4005 | 265.0124 | 240.9063 | 230.6513
| Pumps (elec) | 5.715 | 5.7282 | 5.4311 | 5.807 | 5.347 | 5.2839 | 5.3365 | 5.9358 | 5.2182 | 5.5599 | 6.1199 | 5.4101 | 6.367 | 5.9805 | 6.2907 | 7.1398
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 1.4537 | 21.5063 | 85.0155 | 62.024 | 21.7534 | 184.479 | 11.9059 | 98.0334 | 188.6246 | 40.1524 | 111.4429 | 186.0037 | 140.0496 | 180.8145 | 168.856 | 228.4589
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1744.1437 | 1702.0697 | 1774.8954 | 1660.4636 | 1481.1948 | 1790.5184 | 1373.2824 | 1635.8369 | 1671.8542 | 1436.2817 | 1530.2694 | 1564.315 | 1540.8214 | 1522.2804 | 1489.7411 | 1563.9523
Gas (MJ/m2)
| Heating (gas) | 675.1744 | 816.5751 | 861.5855 | 951.5012 | 944.3377 | 854.89 | 989.8949 | 996.1462 | 874.4483 | 1049.3952 | 980.2577 | 861.5882 | 1034.574 | 953.2414 | 1042.697 | 1282.9304
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 7.3896 | 8.8118 | 7.9863 | 10.1866 | 9.9211 | 8.9695 | 11.0988 | 11.2644 | 11.0568 | 11.827 | 12.2187 | 12.1687 | 13.031 | 13.1887 | 14.3927 | 16.0278
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 732.0827 | 874.9057 | 919.0906 | 1011.2092 | 1003.7802 | 913.3809 | 1050.5125 | 1056.932 | 935.0238 | 1110.7437 | 1041.9952 | 923.2757 | 1097.1265 | 1015.949 | 1106.6086 | 1348.4796
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2476.2264 | 2576.9753 | 2693.9887 | 2671.6728 | 2484.9751 | 2703.8993 | 2423.7949 | 2692.7663 | 2606.878 | 2547.0254 | 2572.2672 | 2487.5907 | 2637.9478 | 2538.2294 | 2596.3496 | 2912.4345
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 341.2837 | 338.1764 | 346.7441 | 334.6738 | 337.5876 | 333.2076 | 297.836 | 357.58 | 345.5156 | 319.8612 | 342.407 | 353.2022 | 362.8237 | 361.0662 | 356.4717 | 384.1203
| Feb | 341.1647 | 335.9403 | 366.0071 | 346.7781 | 315.6549 | 334.3545 | 288.0944 | 339.1506 | 344.6616 | 304.293 | 304.9452 | 321.2601 | 336.4214 | 354.0571 | 345.5941 | 374.3227
| Mar | 344.2656 | 324.3942 | 399.9372 | 344.0429 | 331.715 | 343.9857 | 275.349 | 327.7504 | 355.6471 | 302.5532 | 298.1243 | 349.696 | 323.9248 | 315.286 | 315.8796 | 355.782
| Apr | 349.9591 | 340.5902 | 393.2889 | 332.7575 | 365.105 | 359.9796 | 297.2486 | 309.9622 | 388.9409 | 282.9587 | 286.5467 | 326.6706 | 289.7175 | 309.8001 | 302.7473 | 328.2236
| May | 370.1841 | 375.0484 | 421.4825 | 346.8568 | 301.9706 | 424.9799 | 292.6826 | 329.1711 | 386.725 | 294.6748 | 324.4814 | 350.7617 | 319.3273 | 319.7827 | 294.9933 | 302.6031
| Jun | 378.5947 | 379.5134 | 501.8471 | 366.007 | 304.5512 | 482.495 | 296.0564 | 372.0616 | 421.8123 | 302.722 | 354.4961 | 376.3503 | 346.9704 | 348.4739 | 308.7626 | 308.444
| Jul | 368.1874 | 383.2189 | 439.6243 | 388.0359 | 309.5982 | 457.3235 | 310.3714 | 379.6931 | 426.0532 | 317.7689 | 358.6553 | 372.2931 | 342.4232 | 352.7567 | 322.9446 | 296.713
| Aug | 375.4312 | 388.4587 | 440.6621 | 371.5463 | 322.2976 | 424.1082 | 304.8888 | 381.0061 | 370.4119 | 309.0631 | 349.1539 | 370.6694 | 342.9949 | 335.4691 | 315.4236 | 287.7847
| Sep | 369.6522 | 373.3382 | 408.1464 | 353.939 | 330.0312 | 425.2847 | 336.836 | 355.0258 | 373.8923 | 312.015 | 330.0375 | 377.4139 | 323.6546 | 317.791 | 298.1295 | 287.8932
| Oct | 363.2726 | 355.3349 | 390.0783 | 346.9539 | 345.9157 | 379.8381 | 302.3991 | 328.3486 | 365.9962 | 283.5591 | 310.9007 | 358.3559 | 294.3651 | 308.1546 | 296.7608 | 336.167
| Nov | 348.1232 | 338.9538 | 373.8217 | 321.3521 | 315.2254 | 328.8888 | 286.4368 | 313.5545 | 326.6394 | 318.3641 | 310.4535 | 329.4281 | 324.5482 | 308.3873 | 326.8534 | 350.959
| Dec | 338.6306 | 329.6335 | 354.6997 | 350.1256 | 338.3257 | 340.4383 | 297.5975 | 335.7024 | 339.3018 | 325.5272 | 324.1053 | 345.6456 | 334.8043 | 363.2271 | 337.4644 | 370.7125
Time of Peak Electrical Demand
| Jan | 06-JAN-13:09 | 11-JAN-07:10 | 26-JAN-15:00 | 02-JAN-07:10 | 26-JAN-13:00 | 30-JAN-16:00 | 17-JAN-07:10 | 17-JAN-07:10 | 04-JAN-07:10 | 03-JAN-17:00 | 27-JAN-07:10 | 06-JAN-07:10 | 06-JAN-07:10 | 06-JAN-08:09 | 09-JAN-07:10 | 12-JAN-09:09
| Feb | 22-FEB-13:00 | 23-FEB-14:50 | 28-FEB-17:19 | 14-FEB-07:10 | 10-FEB-10:00 | 07-FEB-17:10 | 15-FEB-17:49 | 06-FEB-07:10 | 14-FEB-14:00 | 15-FEB-07:10 | 09-FEB-07:10 | 06-FEB-07:10 | 07-FEB-07:10 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
| Mar | 13-MAR-15:50 | 24-MAR-13:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-12:09 | 21-MAR-15:20 | 13-MAR-06:10 | 20-MAR-06:10 | 02-MAR-14:00 | 20-MAR-06:10 | 20-MAR-08:09 | 30-MAR-13:00 | 13-MAR-06:10 | 03-MAR-07:10 | 27-MAR-06:10 | 14-MAR-07:10
| Apr | 03-APR-14:09 | 21-APR-14:00 | 26-APR-16:19 | 14-APR-15:00 | 11-APR-16:00 | 21-APR-14:00 | 13-APR-15:00 | 04-APR-15:00 | 21-APR-16:00 | 12-APR-08:00 | 28-APR-16:00 | 26-APR-13:00 | 10-APR-08:09 | 06-APR-16:00 | 03-APR-08:09 | 03-APR-06:10
| May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-16:19 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:20 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-13:00 | 04-MAY-14:00 | 04-MAY-16:00 | 18-MAY-12:00 | 31-MAY-12:09 | 04-MAY-16:00 | 31-MAY-16:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-12:09 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 15-JUN-16:19
| Jul | 13-JUL-14:00 | 31-JUL-14:30 | 19-JUL-16:00 | 03-JUL-15:39 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-13:00 | 13-JUL-16:10 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
| Aug | 21-AUG-14:39 | 31-AUG-13:00 | 01-AUG-16:30 | 17-AUG-13:00 | 08-AUG-12:00 | 18-AUG-14:00 | 15-AUG-12:09 | 17-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:00 | 25-SEP-12:50 | 20-SEP-14:50 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:49 | 01-SEP-15:09 | 27-SEP-15:00 | 06-SEP-12:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 25-SEP-06:10
| Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-13:00 | 12-OCT-15:00 | 30-OCT-12:00 | 03-OCT-15:00 | 30-OCT-13:20 | 20-OCT-14:30 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-16:49 | 05-OCT-14:00 | 30-OCT-06:10 | 19-OCT-16:00 | 30-OCT-06:10 | 30-OCT-08:09
| Nov | 07-NOV-14:00 | 27-NOV-17:19 | 13-NOV-13:00 | 30-NOV-07:10 | 08-NOV-11:00 | 10-NOV-16:40 | 16-NOV-16:00 | 28-NOV-17:00 | 13-NOV-17:00 | 28-NOV-07:10 | 02-NOV-16:49 | 10-NOV-13:00 | 27-NOV-07:10 | 30-NOV-07:10 | 24-NOV-07:10 | 02-NOV-08:09
| Dec | 15-DEC-17:30 | 19-DEC-17:30 | 06-DEC-17:19 | 18-DEC-07:10 | 18-DEC-11:50 | 05-DEC-16:30 | 26-DEC-07:10 | 21-DEC-07:10 | 18-DEC-07:10 | 11-DEC-07:10 | 26-DEC-07:10 | 11-DEC-07:10 | 20-DEC-07:10 | 11-DEC-07:10 | 21-DEC-07:10 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 25048.48 | 27150.42 | 25173.59 | 25448.98 | 21608.4 | 28157.65 | 20532.02 | 26642.98 | 24985.72 | 14131.65 | 24970.28 | 23579.6 | 24702.74 | 24348.95 | 24074.27 | 26852.44
| Total Source Energy (MJ/m2) | 6584.76 | 7137.32 | 6617.65 | 6690.05 | 5680.43 | 7402.1 | 5397.47 | 7003.92 | 6568.26 | 3714.94 | 6564.2 | 6198.62 | 6493.87 | 6400.87 | 6328.66 | 7058.99
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 2.06 | 30.43 | 120.3 | 87.77 | 30.78 | 261.05 | 16.85 | 138.72 | 266.92 | 56.82 | 157.7 | 263.21 | 198.18 | 255.87 | 238.95 | 323.29
| Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
| Total Building | 242.53 | 270.91 | 360.78 | 328.25 | 271.26 | 501.53 | 257.33 | 379.2 | 507.4 | 297.3 | 398.18 | 503.69 | 438.66 | 496.35 | 479.43 | 563.77
Emissions
| Carbon Equivalent (kg) | 555655.9079 | 659933.3949 | 629207.5585 | 609834.842 | 251766.5695 | 700774.4652 | 241646.2196 | 538957.3656 | 785791.0149 | 186731.7076 | 933574.4471 | 738566.3047 | 632559.9943 | 657514.236 | 614734.6184 | 557516.6877
| CO2 (kg) | 1315460 | 1678760 | 1513590 | 1427060 | 687278.6512 | 1692420 | 660962.2311 | 1255510 | 1866830 | 482718.9688 | 2195600 | 1756340 | 1502240 | 1568550 | 1461520 | 1432130
| NOX (kg) | 2195.7902 | 2136.0871 | 2415.7212 | 2550.6048 | 598.5194 | 2642.9217 | 576.4809 | 2281.6354 | 3118.5269 | 621.7571 | 3809.4143 | 2926.6416 | 2541.927 | 2609.7116 | 2465.9066 | 1701.9934
| SO2 (kg) | 7889.4482 | 8579.8568 | 7542.6122 | 6159.5425 | 4555.3759 | 10408.3676 | 4223.6139 | 6310.9334 | 7715.3306 | 1174.174 | 10898.2816 | 7219.1067 | 3843.7893 | 4296.0505 | 3716.4048 | 8413.6762
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0362 | 0.0245 | 0.0208 | 0.0229 | 0.0025 | 0.0199 | 0.0023 | 0.0259 | 0.0304 | 0.005 | 0.0333 | 0.0285 | 0.0285 | 0.0302 | 0.0275 | 0.029
| Water for Electricity (m3) | 976.3347 | 2926.41 | 55710 | 10954.8 | 27480.2 | 51904.7 | 25478.2 | 392.4432 | 8021.76 | 15505.8 | 2508.66 | 7505.78 | 2525.96 | 101892 | 2442.22 | 1688.41

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.05 | 0.05 | 12.29 | 71.86 | 3666.11
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 6.41
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
INFIL_SCH | Fraction | Through 12/31 | SummerDesign, WinterDesign | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
RADIOLOGY_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 11.64 | 70.08 | 3654.17
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | Sat, WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
HTGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | Sat, WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
AHU-1_MinOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
AHU-1_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 17 | 102 | 5151
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU-2_Fan_Sch | Fraction | Through 12/31 | WD, Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600