## BuildingSummary
Building Summary Small Hotel new construction
|  | Value | Data Source
Program
| Building Name | Small Hotel Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.62811
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.37189
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.25 | See Reference Building Technical Report
HVAC
| System Type | MZ-CAV common areas, PTACs guest rooms | 2003 CBECS
| Heating Type | Gas furnace, unit heater, PTAC electric heat | 2003 CBECS
| Cooling Type | DX | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57847
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.070528
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 11.8403 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.18717
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 9.6875 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.13229
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 13.9931 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.13223
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 16.1458 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.13229
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13229
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.1323
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.1323
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 12.9167 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.1323
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 6.4583 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.13227
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.13222
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 9.6875 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.1323
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 11.8403 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.13225
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57864
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13226
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57858
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.058175
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.40695
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.13225
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13224
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.13232
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13221
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57849
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57858
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.058175
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.57847
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.40695
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.13225
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13224
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13224
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.13232
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.13226
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.13226
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.13221
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.57849
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.9753
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 5.3819 | 0 |  |  |  | 0.25 | 31.355 |  | 0.45493
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.97512
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.80368
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52901
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 11.8403 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.52901
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52901
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52898
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52902
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.52903
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 11.8403 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.52902
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 11.8403 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.52903
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 8.6111 | 0 |  |  |  |  | 0 |  | 0.52884
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 6.4583 | 0 |  |  |  |  | 0 |  | 0.97528
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 3.1231 | 88.1153 | 9.1306 | 82.0032 |  | 34.8301 | 6.663 | 96.3435 | 6.2231 | 12.0231 | 111.6509 | 27.3736 | 32.6486 | 9.4333 | 6.2759 | 1.1875
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.2051
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| GUESTROOM101 PTAC DXCOIL | 1.8363 | 1.9103 | 1.8261 | 1.7313 | 1.4454 | 1.5155 | 1.7606 | 1.683 | 1.5124 | 1.4229 | 1.6811 | 1.5186 | 1.6319 | 1.4758 | 1.4193 | 1.2153
| GUESTROOM102 PTAC DXCOIL | 1.8583 | 1.9334 | 1.8534 | 1.7526 | 1.4682 | 1.5376 | 1.8078 | 1.7033 | 1.5355 | 1.4533 | 1.7015 | 1.5411 | 1.6527 | 1.5005 | 1.4419 | 1.2404
| GUESTROOM103 PTAC DXCOIL | 2.0066 | 2.0861 | 2.0259 | 1.8687 | 1.5588 | 1.6376 | 1.8203 | 1.7922 | 1.5945 | 1.4963 | 1.7855 | 1.5873 | 1.7273 | 1.5535 | 1.471 | 1.2467
| GUESTROOM104 PTAC DXCOIL | 1.9201 | 1.8884 | 1.7387 | 1.6584 | 1.3409 | 1.4427 | 1.0987 | 1.5902 | 1.4614 | 1.1742 | 1.5705 | 1.4169 | 1.5115 | 1.3416 | 1.2355 | 0.96982
| GUESTROOM105 PTAC DXCOIL | 1.9204 | 1.8775 | 1.7113 | 1.6901 | 1.4339 | 1.4903 | 1.2402 | 1.6394 | 1.6131 | 1.2934 | 1.6257 | 1.5859 | 1.5706 | 1.4956 | 1.3733 | 1.1365
| GUESTROOM201 PTAC DXCOIL | 2.6719 | 2.7281 | 2.8819 | 2.3362 | 2.1232 | 2.501 | 2.4259 | 2.1636 | 2.3282 | 2.0555 | 2.182 | 2.3072 | 2.1267 | 2.2443 | 2.1166 | 1.8852
| GUESTROOM202_205 PTAC DXCOIL | 7.9654 | 8.3008 | 8.5772 | 7.7307 | 6.7783 | 7.5488 | 9.0035 | 7.632 | 7.7995 | 7.4296 | 7.6953 | 7.8422 | 7.5234 | 7.6745 | 7.4389 | 7.14
| GUESTROOM206_208 PTAC DXCOIL | 6.3114 | 6.5799 | 6.8457 | 6.1504 | 5.4308 | 6.0778 | 7.6473 | 6.057 | 6.2686 | 6.1114 | 6.1255 | 6.3018 | 6.0668 | 6.2202 | 6.0923 | 5.8678
| GUESTROOM209_212 PTAC DXCOIL | 7.8086 | 8.1285 | 8.3851 | 7.5655 | 6.573 | 7.3232 | 8.7756 | 7.46 | 7.5599 | 7.1983 | 7.5202 | 7.6009 | 7.3467 | 7.4372 | 7.1997 | 6.9121
| GUESTROOM213 PTAC DXCOIL | 2.2018 | 2.2912 | 2.4091 | 2.1133 | 1.8616 | 2.1371 | 2.3843 | 2.0675 | 2.1123 | 2.0032 | 2.0799 | 2.1057 | 2.0251 | 2.0704 | 2.0007 | 1.8997
| GUESTROOM214 PTAC DXCOIL | 2.1408 | 2.1231 | 2.1698 | 1.9358 | 1.675 | 2.0358 | 1.6144 | 1.8814 | 2.0109 | 1.67 | 1.8821 | 1.9674 | 1.8372 | 1.89 | 1.7875 | 1.6014
| GUESTROOM215_218 PTAC DXCOIL | 8.142 | 8.072 | 7.9827 | 7.6953 | 6.6771 | 7.6761 | 6.6265 | 7.7335 | 8.0886 | 6.7119 | 7.7513 | 8.003 | 7.5484 | 7.6234 | 7.1162 | 6.5538
| GUESTROOM219 PTAC DXCOIL | 2.4202 | 2.3902 | 2.5006 | 2.3849 | 2.1651 | 2.4617 | 2.1457 | 2.3579 | 2.6179 | 2.1764 | 2.3644 | 2.596 | 2.3086 | 2.4739 | 2.2964 | 2.1665
| GUESTROOM220_223 PTAC DXCOIL | 7.6152 | 7.5431 | 7.4271 | 7.1466 | 5.9862 | 6.9145 | 5.9113 | 7.0201 | 7.2467 | 6.0029 | 7.1951 | 7.1593 | 6.9951 | 6.8169 | 6.3849 | 5.8242
| GUESTROOM224 PTAC DXCOIL | 2.1194 | 2.0867 | 2.1121 | 1.9102 | 1.6784 | 1.9974 | 1.6292 | 1.9349 | 2.0232 | 1.6817 | 1.8786 | 1.9836 | 1.8219 | 1.896 | 1.7826 | 1.6093
| GUESTROOM301 PTAC DXCOIL | 2.6636 | 2.7075 | 2.8925 | 2.3326 | 2.1042 | 2.5109 | 2.4036 | 2.1562 | 2.3188 | 2.0442 | 2.1729 | 2.2916 | 2.1113 | 2.2308 | 2.1056 | 1.8868
| GUESTROOM302_305 PTAC DXCOIL | 7.9595 | 8.2961 | 8.6319 | 7.7541 | 6.7745 | 7.6506 | 9.0426 | 7.6498 | 7.8421 | 7.4506 | 7.7144 | 7.875 | 7.5098 | 7.7093 | 7.4686 | 7.2292
| GUESTROOM306_308 PTAC DXCOIL | 6.3979 | 6.6796 | 7.0081 | 6.2585 | 5.5599 | 6.3046 | 7.8629 | 6.1814 | 6.4505 | 6.283 | 6.2358 | 6.4791 | 6.1057 | 6.388 | 6.2727 | 6.0907
| GUESTROOM309_312 PTAC DXCOIL | 7.9466 | 8.2839 | 8.6194 | 7.7446 | 6.7611 | 7.6373 | 9.0324 | 7.6421 | 7.8306 | 7.4407 | 7.7062 | 7.8632 | 7.5288 | 7.6965 | 7.458 | 7.2183
| GUESTROOM313 PTAC DXCOIL | 2.2479 | 2.3393 | 2.4877 | 2.1701 | 1.9162 | 2.2423 | 2.4534 | 2.1188 | 2.1968 | 2.0787 | 2.1394 | 2.1836 | 2.082 | 2.1509 | 2.0809 | 1.9965
| GUESTROOM314 PTAC DXCOIL | 2.1873 | 2.1607 | 2.2717 | 1.9973 | 1.7206 | 2.1453 | 1.675 | 1.9293 | 2.0954 | 1.738 | 1.9398 | 2.044 | 1.912 | 1.9697 | 1.8716 | 1.6917
| GUESTROOM315_318 PTAC DXCOIL | 7.87 | 7.8067 | 7.7725 | 7.1789 | 6.2962 | 7.3904 | 6.2851 | 7.2949 | 7.6805 | 6.3683 | 7.1003 | 7.5825 | 6.8735 | 7.2364 | 6.8031 | 6.2607
| GUESTROOM319 PTAC DXCOIL | 2.0731 | 2.0567 | 2.0577 | 1.8921 | 1.686 | 1.9857 | 1.6792 | 1.9206 | 2.0568 | 1.7052 | 1.8691 | 2.028 | 1.8116 | 1.9361 | 1.8194 | 1.6716
| GUESTROOM320_323 PTAC DXCOIL | 7.7727 | 7.7094 | 7.6697 | 7.0822 | 6.1753 | 7.2534 | 6.1656 | 7.2 | 7.5343 | 6.2479 | 7.0063 | 7.4369 | 6.7803 | 7.098 | 6.6759 | 6.1362
| GUESTROOM324 PTAC DXCOIL | 2.1686 | 2.1385 | 2.2191 | 1.9728 | 1.727 | 2.1107 | 1.6932 | 1.9274 | 2.104 | 1.751 | 1.9275 | 2.0563 | 1.8971 | 1.9724 | 1.8644 | 1.698
| GUESTROOM401 PTAC DXCOIL | 3.2817 | 3.3725 | 3.6495 | 2.9445 | 2.545 | 3.1564 | 2.7124 | 2.6875 | 2.8618 | 2.4275 | 2.6664 | 2.7544 | 2.5509 | 2.6548 | 2.4942 | 2.0484
| GUESTROOM402_405 PTAC DXCOIL | 10.0147 | 10.4447 | 10.7895 | 9.794 | 8.3868 | 10.0359 | 10.0308 | 9.6013 | 9.9757 | 8.6787 | 9.5647 | 9.6714 | 9.2342 | 9.4212 | 8.8647 | 7.5652
| GUESTROOM406_408 PTAC DXCOIL | 8.0831 | 8.4195 | 8.7812 | 7.9148 | 6.8742 | 8.242 | 8.6774 | 7.7949 | 8.1798 | 7.2568 | 7.7699 | 7.9347 | 7.4893 | 7.7506 | 7.3595 | 6.3736
| GUESTROOM409_412 PTAC DXCOIL | 10.0284 | 10.4383 | 10.7838 | 9.7957 | 8.3885 | 10.039 | 10.0373 | 9.6078 | 9.982 | 8.688 | 9.6045 | 9.6779 | 9.2411 | 9.4281 | 8.8724 | 7.5736
| GUESTROOM413 PTAC DXCOIL | 2.8172 | 2.9332 | 3.1152 | 2.7489 | 2.3802 | 2.9326 | 2.7224 | 2.6654 | 2.8126 | 2.4452 | 2.6495 | 2.7007 | 2.5553 | 2.6426 | 2.4914 | 2.0896
| GUESTROOM414 PTAC DXCOIL | 2.8046 | 2.8338 | 3.0421 | 2.6588 | 2.1876 | 2.8368 | 1.9941 | 2.5769 | 2.6979 | 2.1847 | 2.5399 | 2.5493 | 2.4261 | 2.4461 | 2.2897 | 1.8667
| GUESTROOM415_418 PTAC DXCOIL | 10.0864 | 10.1356 | 10.2431 | 9.6102 | 7.9041 | 9.8056 | 7.384 | 9.3594 | 9.8066 | 7.8958 | 9.2456 | 9.3867 | 8.8445 | 8.9394 | 8.3201 | 6.8264
| GUESTROOM419 PTAC DXCOIL | 2.6242 | 2.6491 | 2.7283 | 2.4967 | 2.0731 | 2.5907 | 1.9182 | 2.4345 | 2.5728 | 2.0666 | 2.401 | 2.4533 | 2.2947 | 2.3389 | 2.1784 | 1.7613
| GUESTROOM420_423 PTAC DXCOIL | 10.0257 | 10.0747 | 10.1605 | 9.549 | 7.8335 | 9.7225 | 7.3185 | 9.3026 | 9.7223 | 7.828 | 9.1891 | 9.3044 | 8.7892 | 8.8615 | 8.2496 | 6.7586
| GUESTROOM424 PTAC DXCOIL | 2.7892 | 2.7994 | 2.9899 | 2.638 | 2.1936 | 2.803 | 2.0113 | 2.5632 | 2.7087 | 2.1921 | 2.5331 | 2.5682 | 2.422 | 2.4566 | 2.3004 | 1.8736
| PSZ-HEATCOOL:1_COOLC DXCOIL | 8.6251 | 8.5489 | 8.2503 | 8.4013 | 7.516 | 7.6446 | 6.6094 | 8.0608 | 8.7281 | 7.2336 | 8.047 | 8.653 | 8.1285 | 8.2899 | 7.5967 | 6.2016
| PSZ-HEATCOOL:10_COOLC DXCOIL | 4.6633 | 4.6827 | 4.6502 | 4.2519 | 3.5432 | 4.1264 | 3.8018 | 4.2827 | 4.2761 | 3.6576 | 4.295 | 4.2135 | 4.1595 | 4.053 | 3.8786 | 3.3393
| PSZ-HEATCOOL:11_COOLC DXCOIL | 4.3703 | 4.3865 | 4.4223 | 3.9652 | 3.1768 | 3.8659 | 3.4576 | 3.9969 | 3.8852 | 3.3304 | 4.007 | 3.8009 | 3.8698 | 3.6757 | 3.5581 | 3.0668
| PSZ-HEATCOOL:12_COOLC DXCOIL | 6.8909 | 7.0764 | 7.1462 | 6.4622 | 4.8895 | 6.4229 | 4.6351 | 6.3291 | 6.1339 | 4.9477 | 6.1914 | 5.7012 | 5.8567 | 5.4885 | 5.2616 | 4.5296
| PSZ-HEATCOOL:2_COOLC DXCOIL | 18.8712 | 19.4209 | 20.0523 | 18.6806 | 17.4092 | 18.5742 | 15.4603 | 17.9489 | 15.7173 | 15.2831 | 18.1647 | 15.7223 | 18.2918 | 14.3925 | 18.6088 | 11.5185
| PSZ-HEATCOOL:3_COOLC DXCOIL | 1.2675 | 1.3148 | 1.2763 | 1.2602 | 1.2181 | 1.1669 | 1.1723 | 1.1808 | 1.2423 | 1.1193 | 1.1867 | 1.2459 | 1.1963 | 1.2134 | 1.1022 | 0.93911
| PSZ-HEATCOOL:4_COOLC DXCOIL | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 10.6599 | 8.5734 | 10.6599 | 10.4175 | 9.7293 | 10.6599 | 10.5457 | 10.6599 | 8.7987 | 10.6599 | 7.106
| PSZ-HEATCOOL:5_COOLC DXCOIL | 1.1609 | 1.2054 | 1.0665 | 1.0638 | 0.88538 | 0.84158 | 0.84316 | 1.019 | 0.82966 | 0.77202 | 1.0137 | 0.83504 | 0.98451 | 0.82227 | 0.793 | 0.59058
| PSZ-HEATCOOL:6_COOLC DXCOIL | 7.9091 | 7.7664 | 6.9706 | 7.181 | 5.9031 | 6.0839 | 4.8808 | 7.1514 | 5.9647 | 5.2328 | 7.1457 | 5.9474 | 6.8575 | 5.6248 | 5.8855 | 4.738
| PSZ-HEATCOOL:7_COOLC DXCOIL | 28.7679 | 28.3953 | 27.2935 | 27.6728 | 24.9543 | 26.5097 | 23.9408 | 27.4193 | 29.7558 | 24.6872 | 27.4435 | 29.6982 | 27.036 | 28.0584 | 25.6363 | 24.1764
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.2244 | 3.2234 | 3.1827 | 3.19 | 2.8815 | 3.0283 | 2.0449 | 3.0191 | 2.2934 | 1.9042 | 3.0282 | 2.2618 | 3.0611 | 2.127 | 2.9169 | 1.8209
| PSZ-HEATCOOL:9_COOLC DXCOIL | 9.1724 | 8.9693 | 7.7246 | 7.8653 | 6.1036 | 6.1874 | 4.4048 | 7.9706 | 5.6701 | 4.9621 | 7.9367 | 5.5535 | 7.7848 | 5.2355 | 5.8024 | 3.8769
Heating (kW)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.19853 | 0.04015 | 0.24181 | 0 | 0.09968 | 0 | 0.29361 | 0.18538 | 0.07983 | 0.6117 | 0.46157 | 0.79723 | 0.76652 | 0.89004 | 1.3394
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.33201 | 0.14759 | 0.33778 | 0 | 0.17217 | 0 | 0.36755 | 0.25621 | 0.18688 | 0.62667 | 0.49112 | 0.78008 | 0.75111 | 0.85455 | 1.2026
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.37765 | 0.18416 | 0.382 | 0 | 0.21149 | 0.08014 | 0.41454 | 0.30136 | 0.23537 | 0.67639 | 0.54011 | 0.82928 | 0.80121 | 0.90442 | 1.2497
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.15676 | 0.73912 | 0.45127 | 0.80975 | 0.17283 | 0.54498 | 0.34958 | 0.92103 | 0.73344 | 0.62529 | 1.3396 | 1.1239 | 1.5926 | 1.559 | 1.7182 | 2.2616
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.03312 | 0 | 0.04884 | 0 | 0 | 0 | 0.08035 | 0.04111 | 0 | 0.18922 | 0.14822 | 0.25687 | 0.26342 | 0.293 | 0.39307
| GUESTROOM101 PTAC HEAT COIL | 0.55632 | 0.8082 | 0.68417 | 0.86317 | 0.5786 | 0.74686 | 0.63954 | 0.96638 | 0.83431 | 0.76451 | 1.256 | 1.0812 | 1.4227 | 1.3648 | 1.5016 | 1.9055
| GUESTROOM102 PTAC HEAT COIL | 0.55632 | 0.82977 | 0.70314 | 0.88373 | 0.5786 | 0.76542 | 0.63954 | 0.98731 | 0.85488 | 0.783 | 1.2786 | 1.1033 | 1.4462 | 1.3884 | 1.5256 | 1.9296
| GUESTROOM103 PTAC HEAT COIL | 0.55632 | 1.0449 | 0.89946 | 1.0955 | 0.5786 | 0.9637 | 0.76486 | 1.195 | 1.0616 | 0.96383 | 1.4977 | 1.3212 | 1.6722 | 1.6165 | 1.7551 | 2.1669
| GUESTROOM104 PTAC HEAT COIL | 0.55632 | 1.0341 | 0.89365 | 1.0937 | 0.5786 | 0.97229 | 0.75963 | 1.1947 | 1.0598 | 0.9794 | 1.4951 | 1.3199 | 1.6664 | 1.6107 | 1.7487 | 2.1654
| GUESTROOM105 PTAC HEAT COIL | 0.55632 | 0.82056 | 0.69759 | 0.88258 | 0.5786 | 0.76651 | 0.63954 | 0.98754 | 0.85349 | 0.7817 | 1.2804 | 1.106 | 1.4474 | 1.3899 | 1.5272 | 1.9375
| GUESTROOM201 PTAC HEAT COIL | 0.6985 | 1.2969 | 0.99563 | 1.2769 | 0.64977 | 1.0065 | 0.86161 | 1.3552 | 1.141 | 1.0697 | 1.7592 | 1.5065 | 1.9856 | 1.9051 | 2.0919 | 2.5763
| GUESTROOM202_205 PTAC HEAT COIL | 2.2253 | 3.2574 | 2.4936 | 3.3357 | 2.3144 | 2.6793 | 2.5582 | 3.687 | 3.0544 | 3.0508 | 4.7732 | 4.0159 | 5.3714 | 5.0888 | 5.6448 | 6.9998
| GUESTROOM206_208 PTAC HEAT COIL | 1.669 | 2.5087 | 1.9001 | 2.5412 | 1.7358 | 2.0095 | 1.9186 | 2.8257 | 2.3356 | 2.2881 | 3.6949 | 3.104 | 4.1706 | 3.953 | 4.3914 | 5.427
| GUESTROOM209_212 PTAC HEAT COIL | 2.2253 | 3.1823 | 2.4785 | 3.273 | 2.3144 | 2.6793 | 2.5582 | 3.6244 | 2.9958 | 3.0508 | 4.6952 | 3.941 | 5.2847 | 5.0003 | 5.553 | 6.9034
| GUESTROOM213 PTAC HEAT COIL | 0.5845 | 1.0392 | 0.83709 | 1.0552 | 0.5786 | 0.86662 | 0.75942 | 1.1378 | 0.97741 | 0.93546 | 1.4184 | 1.2276 | 1.5724 | 1.503 | 1.6429 | 1.9869
| GUESTROOM214 PTAC HEAT COIL | 0.55632 | 1.0071 | 0.80955 | 1.0252 | 0.5786 | 0.83975 | 0.72383 | 1.1092 | 0.94775 | 0.90833 | 1.389 | 1.1998 | 1.5422 | 1.4727 | 1.6138 | 1.9601
| GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 2.9377 | 2.4785 | 3.169 | 2.3144 | 2.6793 | 2.5582 | 3.5277 | 2.8029 | 3.0508 | 4.4101 | 3.6574 | 5.0048 | 4.7189 | 5.2796 | 6.6534
| GUESTROOM219 PTAC HEAT COIL | 0.6954 | 0.73442 | 0.66806 | 0.79225 | 0.69293 | 0.64253 | 0.69515 | 0.88192 | 0.57203 | 0.68556 | 1.0303 | 0.83647 | 1.1134 | 1.0146 | 1.1397 | 1.4631
| GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 3.0526 | 2.4785 | 3.169 | 2.3144 | 2.6793 | 2.5582 | 3.5277 | 2.8727 | 3.0508 | 4.5861 | 3.8373 | 5.1752 | 4.8895 | 5.4479 | 6.8131
| GUESTROOM224 PTAC HEAT COIL | 0.55632 | 0.92942 | 0.73225 | 0.94866 | 0.5786 | 0.76235 | 0.66973 | 1.0339 | 0.87179 | 0.83079 | 1.3211 | 1.1289 | 1.4781 | 1.4078 | 1.5514 | 1.9066
| GUESTROOM301 PTAC HEAT COIL | 0.75786 | 1.3466 | 1.0318 | 1.3251 | 0.69324 | 1.0427 | 0.90081 | 1.4042 | 1.1844 | 1.1135 | 1.8147 | 1.5586 | 2.0439 | 1.9643 | 2.1525 | 2.6314
| GUESTROOM302_305 PTAC HEAT COIL | 2.2253 | 3.3885 | 2.5851 | 3.4719 | 2.3144 | 2.7168 | 2.5582 | 3.8355 | 3.1843 | 3.0508 | 4.9371 | 4.1689 | 5.5407 | 5.2603 | 5.8201 | 7.1472
| GUESTROOM306_308 PTAC HEAT COIL | 1.669 | 2.7223 | 2.0734 | 2.7556 | 1.7358 | 2.1535 | 1.9511 | 3.0467 | 2.5419 | 2.4214 | 3.9311 | 3.3294 | 4.4117 | 4.1955 | 4.639 | 5.648
| GUESTROOM309_312 PTAC HEAT COIL | 2.2253 | 3.3706 | 2.5733 | 3.4593 | 2.3144 | 2.7084 | 2.5582 | 3.8249 | 3.1753 | 3.0508 | 4.9209 | 4.1538 | 5.5214 | 5.2402 | 5.7992 | 7.124
| GUESTROOM313 PTAC HEAT COIL | 0.66217 | 1.0834 | 0.87192 | 1.1 | 0.63012 | 0.90216 | 0.8118 | 1.1857 | 1.021 | 0.98119 | 1.4717 | 1.2778 | 1.6278 | 1.559 | 1.7002 | 2.0376
| GUESTROOM314 PTAC HEAT COIL | 0.6225 | 1.0578 | 0.8496 | 1.0762 | 0.59247 | 0.87958 | 0.78158 | 1.1626 | 0.99661 | 0.95823 | 1.4484 | 1.2558 | 1.6046 | 1.535 | 1.678 | 2.0157
| GUESTROOM315_318 PTAC HEAT COIL | 2.2253 | 3.3125 | 2.5271 | 3.4091 | 2.3144 | 2.6793 | 2.5582 | 3.7741 | 3.1191 | 3.0508 | 4.8749 | 4.1125 | 5.4741 | 5.1884 | 5.7549 | 7.0819
| GUESTROOM319 PTAC HEAT COIL | 0.55632 | 0.80581 | 0.61963 | 0.82415 | 0.5786 | 0.66983 | 0.63954 | 0.91736 | 0.7428 | 0.76269 | 1.211 | 1.0134 | 1.3719 | 1.3007 | 1.4479 | 1.7969
| GUESTROOM320_323 PTAC HEAT COIL | 2.2253 | 3.3092 | 2.5295 | 3.4106 | 2.3144 | 2.6793 | 2.5582 | 3.7746 | 3.123 | 3.0508 | 4.8698 | 4.1088 | 5.4659 | 5.1799 | 5.7451 | 7.0702
| GUESTROOM324 PTAC HEAT COIL | 0.57925 | 0.99388 | 0.78262 | 1.015 | 0.5786 | 0.81478 | 0.72764 | 1.102 | 0.93533 | 0.89564 | 1.3922 | 1.1969 | 1.5507 | 1.4802 | 1.6254 | 1.97
| GUESTROOM401 PTAC HEAT COIL | 1.0407 | 1.8433 | 1.4283 | 1.8938 | 1.0215 | 1.5102 | 1.2943 | 2.0666 | 1.7685 | 1.6395 | 2.6548 | 2.3209 | 3.0001 | 2.9303 | 3.1729 | 3.8163
| GUESTROOM402_405 PTAC HEAT COIL | 3.0088 | 5.3305 | 4.1298 | 5.6876 | 3.0873 | 4.533 | 3.9537 | 6.4163 | 5.453 | 5.0946 | 8.2156 | 7.136 | 9.2739 | 9.0262 | 9.8046 | 11.7817
| GUESTROOM406_408 PTAC HEAT COIL | 2.4344 | 4.3085 | 3.3369 | 4.5634 | 2.4745 | 3.6373 | 3.2035 | 5.1506 | 4.3927 | 4.0913 | 6.5995 | 5.7457 | 7.4475 | 7.2577 | 7.8783 | 9.4114
| GUESTROOM409_412 PTAC HEAT COIL | 3.0073 | 5.3202 | 4.1242 | 5.6815 | 3.0897 | 4.5304 | 3.9539 | 6.4126 | 5.4504 | 5.0943 | 8.2073 | 7.1286 | 9.2632 | 9.015 | 9.7927 | 11.7678
| GUESTROOM413 PTAC HEAT COIL | 0.97146 | 1.585 | 1.2734 | 1.6728 | 0.99077 | 1.3749 | 1.2174 | 1.8538 | 1.6104 | 1.5131 | 2.3165 | 2.0449 | 2.5888 | 2.5301 | 2.7257 | 3.2268
| GUESTROOM414 PTAC HEAT COIL | 0.94862 | 1.5639 | 1.2538 | 1.6539 | 0.96824 | 1.3546 | 1.1965 | 1.8346 | 1.59 | 1.4922 | 2.2984 | 2.028 | 2.5707 | 2.5106 | 2.7084 | 3.2086
| GUESTROOM415_418 PTAC HEAT COIL | 2.9947 | 5.3055 | 4.1218 | 5.6793 | 3.0789 | 4.526 | 3.9501 | 6.4099 | 5.4437 | 5.0882 | 8.2075 | 7.1335 | 9.263 | 9.0088 | 9.7955 | 11.7695
| GUESTROOM419 PTAC HEAT COIL | 0.78616 | 1.4227 | 1.1013 | 1.5215 | 0.80874 | 1.2087 | 1.046 | 1.7161 | 1.4601 | 1.3549 | 2.2052 | 1.9225 | 2.4942 | 2.4342 | 2.641 | 3.1695
| GUESTROOM420_423 PTAC HEAT COIL | 2.9732 | 5.2762 | 4.0964 | 5.6521 | 3.06 | 4.5024 | 3.9271 | 6.3819 | 5.4176 | 5.0649 | 8.1739 | 7.1013 | 9.2265 | 8.9718 | 9.7574 | 11.7287
| GUESTROOM424 PTAC HEAT COIL | 0.89889 | 1.5348 | 1.2203 | 1.6297 | 0.92431 | 1.3301 | 1.162 | 1.8124 | 1.57 | 1.4757 | 2.2695 | 1.9999 | 2.5381 | 2.4767 | 2.6738 | 3.1709
| REARSTAIRSFLR1 UNIT HEATER COIL | 0 | 0.11068 | 0 | 0.144 | 0 | 0 | 0 | 0.19641 | 0.08854 | 0 | 0.50097 | 0.35578 | 0.68099 | 0.65162 | 0.77008 | 1.2029
| REARSTAIRSFLR2 UNIT HEATER COIL | 0 | 0.2199 | 0.03507 | 0.22202 | 0 | 0.05981 | 0 | 0.25207 | 0.1426 | 0.07676 | 0.50341 | 0.37234 | 0.64783 | 0.61691 | 0.71685 | 1.0509
| REARSTAIRSFLR3 UNIT HEATER COIL | 0 | 0.24903 | 0.06412 | 0.25309 | 0 | 0.08531 | 0 | 0.28561 | 0.17302 | 0.10893 | 0.53748 | 0.40545 | 0.68241 | 0.65296 | 0.75382 | 1.087
| REARSTAIRSFLR4 UNIT HEATER COIL | 0 | 0.57757 | 0.30765 | 0.64598 | 0.0278 | 0.39156 | 0.20338 | 0.75698 | 0.57141 | 0.4689 | 1.1687 | 0.95428 | 1.4179 | 1.3822 | 1.5418 | 2.0793
| REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.0618 | 0 | 0.05789 | 0 | 0 | 0 | 0.06814 | 0 | 0 | 0.28193 | 0.20554 | 0.40593 | 0.4041 | 0.47154 | 0.73625
| REARSTORAGEFLR2 UNIT HEATER COIL | 0 | 0.20124 | 0.0631 | 0.17547 | 0 | 0.05944 | 0 | 0.17431 | 0.11215 | 0.04574 | 0.34801 | 0.27342 | 0.45109 | 0.44409 | 0.50305 | 0.69942
| REARSTORAGEFLR3 UNIT HEATER COIL | 0 | 0.23233 | 0.0905 | 0.20614 | 0 | 0.08792 | 0 | 0.2061 | 0.14122 | 0.08547 | 0.38472 | 0.30886 | 0.48909 | 0.48298 | 0.54206 | 0.73649
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.05392 | 0.48014 | 0.27713 | 0.49701 | 0.05011 | 0.31546 | 0.17737 | 0.55114 | 0.44226 | 0.34528 | 0.83933 | 0.72047 | 1.0143 | 1.0168 | 1.1051 | 1.4068
| PSZ-HEATCOOL:1_HEATC | 24.5027 | 24.9523 | 23.0449 | 23.9838 | 21.5959 | 20.7213 | 19.1703 | 23.9387 | 21.3268 | 21.0503 | 12.7807 | 11.3468 | 13.0307 | 11.8904 | 12.186 | 11.3192
| PSZ-HEATCOOL:10_HEATC | 11.5444 | 6.5641 | 6.5834 | 6.2974 | 10.0725 | 6.0902 | 10.9894 | 6.4968 | 5.8208 | 5.9611 | 6.8087 | 6.0378 | 6.9675 | 6.4697 | 6.9192 | 6.9333
| PSZ-HEATCOOL:11_HEATC | 5.6584 | 6.1065 | 6.25 | 5.8631 | 4.9403 | 5.7561 | 5.4749 | 6.0533 | 5.3743 | 5.5132 | 6.3644 | 5.5674 | 6.5168 | 6.0153 | 6.4965 | 6.561
| PSZ-HEATCOOL:12_HEATC | 8.8304 | 9.5697 | 10.073 | 9.1376 | 7.3102 | 9.0373 | 7.1097 | 9.1003 | 7.9435 | 7.7277 | 9.151 | 7.7346 | 9.0352 | 8.1989 | 8.7446 | 8.5604
| PSZ-HEATCOOL:2_HEATC | 24.1307 | 29.8589 | 26.7431 | 30.632 | 23.8699 | 26.6345 | 28.3501 | 32.8372 | 27.7586 | 29.9799 | 37.2896 | 31.757 | 39.8012 | 36.9775 | 40.7075 | 47.4933
| PSZ-HEATCOOL:3_HEATC | 3.7057 | 1.8191 | 1.7028 | 1.686 | 1.6856 | 1.4973 | 1.6274 | 1.6311 | 1.4191 | 1.5324 | 1.6117 | 1.4207 | 1.6122 | 1.4612 | 1.4543 | 1.2833
| PSZ-HEATCOOL:4_HEATC | 16.6197 | 21.9403 | 18.5109 | 23.6679 | 17.2852 | 20.0108 | 19.1482 | 26.3467 | 21.2855 | 22.7848 | 30.7783 | 25.3463 | 33.2623 | 30.3803 | 34.0465 | 42.1613
| PSZ-HEATCOOL:5_HEATC | 1.4185 | 1.5809 | 1.4038 | 1.4899 | 1.3667 | 1.2392 | 1.346 | 1.4727 | 1.1912 | 1.3049 | 1.5416 | 1.2729 | 1.5898 | 1.4034 | 1.4486 | 1.4233
| PSZ-HEATCOOL:6_HEATC | 14.5799 | 9.7835 | 8.9596 | 10.002 | 8.4653 | 9.0855 | 8.5107 | 10.4289 | 9.4411 | 9.3914 | 11.3362 | 10.2432 | 11.8396 | 11.2329 | 11.8439 | 13.1269
| PSZ-HEATCOOL:7_HEATC | 73.0416 | 74.3716 | 72.1225 | 74.5416 | 71.5579 | 71.8808 | 69.4136 | 75.0961 | 72.8391 | 71.9204 | 76.4312 | 73.9303 | 42.4588 | 41.0359 | 42.0433 | 43.8491
| PSZ-HEATCOOL:8_HEATC | 5.2193 | 6.0758 | 5.1446 | 6.4737 | 4.7205 | 5.3815 | 4.8958 | 7.016 | 5.8377 | 5.8386 | 8.1554 | 6.8578 | 8.8194 | 8.1355 | 8.8873 | 10.8037
| PSZ-HEATCOOL:9_HEATC | 10.0667 | 11.1993 | 9.8423 | 10.8905 | 8.7259 | 9.2975 | 7.9923 | 11.1904 | 9.4629 | 9.2613 | 12.1069 | 10.2661 | 12.6088 | 11.3722 | 12.0343 | 12.8574
HVAC Efficiency
Air Conditioning (COP)
| GUESTROOM101 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM102 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM103 PTAC DXCOIL | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM104 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM105 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM201 PTAC DXCOIL | 3.65 | 3.64 | 3.6 | 3.73 | 3.79 | 3.69 | 3.71 | 3.78 | 3.74 | 3.8 | 3.77 | 3.74 | 3.78 | 3.76 | 3.79 | 3.8
| GUESTROOM202_205 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM206_208 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM209_212 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM213 PTAC DXCOIL | 3.77 | 3.74 | 3.72 | 3.79 | 3.8 | 3.78 | 3.72 | 3.8 | 3.79 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM214 PTAC DXCOIL | 3.78 | 3.79 | 3.77 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM215_218 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM219 PTAC DXCOIL | 3.71 | 3.72 | 3.69 | 3.72 | 3.78 | 3.7 | 3.78 | 3.73 | 3.67 | 3.77 | 3.73 | 3.67 | 3.74 | 3.7 | 3.74 | 3.78
| GUESTROOM220_223 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM224 PTAC DXCOIL | 3.79 | 3.79 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM301 PTAC DXCOIL | 3.65 | 3.64 | 3.6 | 3.73 | 3.79 | 3.69 | 3.72 | 3.78 | 3.74 | 3.8 | 3.77 | 3.74 | 3.79 | 3.76 | 3.79 | 3.8
| GUESTROOM302_305 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM306_308 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM309_312 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM313 PTAC DXCOIL | 3.76 | 3.73 | 3.7 | 3.77 | 3.8 | 3.76 | 3.71 | 3.79 | 3.77 | 3.8 | 3.78 | 3.77 | 3.8 | 3.78 | 3.8 | 3.8
| GUESTROOM314 PTAC DXCOIL | 3.77 | 3.78 | 3.75 | 3.8 | 3.8 | 3.78 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM315_318 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM319 PTAC DXCOIL | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM320_323 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM324 PTAC DXCOIL | 3.77 | 3.78 | 3.76 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.79 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8
| GUESTROOM401 PTAC DXCOIL | 3.51 | 3.48 | 3.42 | 3.59 | 3.68 | 3.54 | 3.64 | 3.65 | 3.61 | 3.71 | 3.65 | 3.63 | 3.68 | 3.66 | 3.7 | 3.8
| GUESTROOM402_405 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM406_408 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM409_412 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM413 PTAC DXCOIL | 3.62 | 3.59 | 3.55 | 3.63 | 3.72 | 3.59 | 3.64 | 3.65 | 3.62 | 3.71 | 3.66 | 3.65 | 3.68 | 3.66 | 3.7 | 3.79
| GUESTROOM414 PTAC DXCOIL | 3.62 | 3.61 | 3.56 | 3.66 | 3.77 | 3.61 | 3.8 | 3.68 | 3.65 | 3.77 | 3.68 | 3.68 | 3.71 | 3.71 | 3.75 | 3.8
| GUESTROOM415_418 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM419 PTAC DXCOIL | 3.66 | 3.66 | 3.64 | 3.7 | 3.8 | 3.67 | 3.8 | 3.71 | 3.68 | 3.8 | 3.72 | 3.71 | 3.74 | 3.73 | 3.77 | 3.8
| GUESTROOM420_423 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM424 PTAC DXCOIL | 3.62 | 3.62 | 3.58 | 3.66 | 3.77 | 3.62 | 3.8 | 3.68 | 3.64 | 3.77 | 3.69 | 3.68 | 3.71 | 3.7 | 3.74 | 3.8
| PSZ-HEATCOOL:1_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:10_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:11_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:12_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:2_COOLC DXCOIL | 3.67 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:3_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:4_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:5_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:6_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:7_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-HEATCOOL:9_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
Heating Efficiency (%)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:9_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| All GuestRoom & UnitHeater systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:10_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:11_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:12_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:3_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:4_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:5_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:6_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:7_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:9_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.05
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0.01 | 0.01 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.08
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
| GUESTROOM101 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.07
| GUESTROOM102 PTACFAN | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.11 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.07
| GUESTROOM103 PTACFAN | 0.1 | 0.11 | 0.11 | 0.1 | 0.09 | 0.1 | 0.11 | 0.09 | 0.1 | 0.09 | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.08
| GUESTROOM104 PTACFAN | 0.1 | 0.1 | 0.1 | 0.09 | 0.08 | 0.09 | 0.07 | 0.09 | 0.09 | 0.07 | 0.09 | 0.09 | 0.09 | 0.08 | 0.07 | 0.06
| GUESTROOM105 PTACFAN | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.07 | 0.09 | 0.1 | 0.08 | 0.09 | 0.1 | 0.09 | 0.09 | 0.08 | 0.07
| GUESTROOM201 PTACFAN | 0.15 | 0.16 | 0.17 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.11
| GUESTROOM202_205 PTACFAN | 0.42 | 0.43 | 0.47 | 0.43 | 0.41 | 0.46 | 0.54 | 0.41 | 0.47 | 0.45 | 0.42 | 0.47 | 0.43 | 0.46 | 0.45 | 0.43
| GUESTROOM206_208 PTACFAN | 0.33 | 0.35 | 0.38 | 0.35 | 0.33 | 0.37 | 0.46 | 0.33 | 0.38 | 0.37 | 0.34 | 0.38 | 0.34 | 0.38 | 0.37 | 0.35
| GUESTROOM209_212 PTACFAN | 0.4 | 0.42 | 0.46 | 0.42 | 0.4 | 0.44 | 0.53 | 0.4 | 0.46 | 0.43 | 0.41 | 0.46 | 0.41 | 0.45 | 0.43 | 0.42
| GUESTROOM213 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.11 | 0.13 | 0.14 | 0.12 | 0.13 | 0.12 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.11
| GUESTROOM214 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.11 | 0.1
| GUESTROOM215_218 PTACFAN | 0.45 | 0.45 | 0.48 | 0.44 | 0.4 | 0.46 | 0.4 | 0.42 | 0.49 | 0.41 | 0.43 | 0.48 | 0.43 | 0.46 | 0.43 | 0.4
| GUESTROOM219 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.13 | 0.15 | 0.13 | 0.14 | 0.16 | 0.13 | 0.14 | 0.16 | 0.14 | 0.15 | 0.14 | 0.13
| GUESTROOM220_223 PTACFAN | 0.41 | 0.41 | 0.43 | 0.4 | 0.36 | 0.42 | 0.36 | 0.38 | 0.44 | 0.36 | 0.38 | 0.43 | 0.39 | 0.41 | 0.39 | 0.35
| GUESTROOM224 PTACFAN | 0.12 | 0.12 | 0.13 | 0.11 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.11 | 0.1
| GUESTROOM301 PTACFAN | 0.15 | 0.16 | 0.17 | 0.14 | 0.13 | 0.15 | 0.15 | 0.13 | 0.14 | 0.12 | 0.13 | 0.14 | 0.13 | 0.13 | 0.13 | 0.11
| GUESTROOM302_305 PTACFAN | 0.42 | 0.43 | 0.48 | 0.43 | 0.41 | 0.46 | 0.55 | 0.41 | 0.47 | 0.45 | 0.42 | 0.48 | 0.43 | 0.47 | 0.45 | 0.44
| GUESTROOM306_308 PTACFAN | 0.34 | 0.35 | 0.4 | 0.36 | 0.34 | 0.38 | 0.47 | 0.34 | 0.39 | 0.38 | 0.35 | 0.39 | 0.35 | 0.39 | 0.38 | 0.37
| GUESTROOM309_312 PTACFAN | 0.41 | 0.43 | 0.48 | 0.43 | 0.41 | 0.46 | 0.55 | 0.41 | 0.47 | 0.45 | 0.42 | 0.48 | 0.43 | 0.46 | 0.45 | 0.44
| GUESTROOM313 PTACFAN | 0.12 | 0.13 | 0.14 | 0.13 | 0.12 | 0.14 | 0.15 | 0.12 | 0.13 | 0.13 | 0.12 | 0.13 | 0.12 | 0.13 | 0.13 | 0.12
| GUESTROOM314 PTACFAN | 0.12 | 0.12 | 0.14 | 0.12 | 0.1 | 0.13 | 0.1 | 0.11 | 0.13 | 0.1 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.1
| GUESTROOM315_318 PTACFAN | 0.43 | 0.43 | 0.46 | 0.42 | 0.38 | 0.45 | 0.38 | 0.4 | 0.46 | 0.38 | 0.41 | 0.46 | 0.41 | 0.44 | 0.41 | 0.38
| GUESTROOM319 PTACFAN | 0.11 | 0.12 | 0.12 | 0.11 | 0.1 | 0.12 | 0.1 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1
| GUESTROOM320_323 PTACFAN | 0.42 | 0.42 | 0.45 | 0.41 | 0.37 | 0.44 | 0.37 | 0.39 | 0.46 | 0.38 | 0.4 | 0.45 | 0.4 | 0.43 | 0.4 | 0.37
| GUESTROOM324 PTACFAN | 0.12 | 0.12 | 0.13 | 0.12 | 0.1 | 0.13 | 0.1 | 0.11 | 0.13 | 0.11 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1
| GUESTROOM401 PTACFAN | 0.19 | 0.2 | 0.22 | 0.18 | 0.15 | 0.19 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16 | 0.17 | 0.15 | 0.16 | 0.15 | 0.12
| GUESTROOM402_405 PTACFAN | 0.54 | 0.57 | 0.63 | 0.57 | 0.51 | 0.61 | 0.61 | 0.54 | 0.6 | 0.52 | 0.54 | 0.58 | 0.54 | 0.57 | 0.54 | 0.46
| GUESTROOM406_408 PTACFAN | 0.44 | 0.46 | 0.52 | 0.47 | 0.42 | 0.5 | 0.52 | 0.44 | 0.49 | 0.44 | 0.44 | 0.48 | 0.44 | 0.47 | 0.44 | 0.39
| GUESTROOM409_412 PTACFAN | 0.54 | 0.57 | 0.63 | 0.57 | 0.51 | 0.61 | 0.61 | 0.54 | 0.6 | 0.52 | 0.54 | 0.58 | 0.54 | 0.57 | 0.54 | 0.46
| GUESTROOM413 PTACFAN | 0.16 | 0.17 | 0.19 | 0.17 | 0.14 | 0.18 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.15 | 0.13
| GUESTROOM414 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14 | 0.11
| GUESTROOM415_418 PTACFAN | 0.55 | 0.57 | 0.62 | 0.56 | 0.48 | 0.59 | 0.45 | 0.53 | 0.59 | 0.48 | 0.52 | 0.57 | 0.51 | 0.54 | 0.5 | 0.41
| GUESTROOM419 PTACFAN | 0.15 | 0.15 | 0.16 | 0.15 | 0.13 | 0.16 | 0.12 | 0.14 | 0.16 | 0.12 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.11
| GUESTROOM420_423 PTACFAN | 0.55 | 0.56 | 0.61 | 0.55 | 0.47 | 0.59 | 0.44 | 0.52 | 0.59 | 0.47 | 0.52 | 0.56 | 0.51 | 0.54 | 0.5 | 0.41
| GUESTROOM424 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.15 | 0.16 | 0.15 | 0.15 | 0.14 | 0.11
| REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.02 | 0.01 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
| REARSTAIRSFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
| REARSTAIRSFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.03 | 0.02 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
| REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02
| REARSTORAGEFLR2 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
| REARSTORAGEFLR3 UNIT HEATERFAN | 0 | 0.01 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02
| REARSTORAGEFLR4 UNIT HEATERFAN | 0 | 0.02 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.05
| PSZ-HEATCOOL:1_FAN | 0.51 | 0.52 | 0.5 | 0.51 | 0.45 | 0.46 | 0.4 | 0.49 | 0.53 | 0.44 | 0.49 | 0.52 | 0.49 | 0.5 | 0.46 | 0.37
| PSZ-HEATCOOL:10_FAN | 0.24 | 0.25 | 0.27 | 0.24 | 0.21 | 0.25 | 0.23 | 0.23 | 0.26 | 0.22 | 0.23 | 0.25 | 0.23 | 0.24 | 0.23 | 0.2
| PSZ-HEATCOOL:11_FAN | 0.22 | 0.23 | 0.25 | 0.22 | 0.19 | 0.23 | 0.21 | 0.21 | 0.23 | 0.2 | 0.21 | 0.23 | 0.21 | 0.22 | 0.21 | 0.19
| PSZ-HEATCOOL:12_FAN | 0.36 | 0.38 | 0.43 | 0.37 | 0.3 | 0.39 | 0.28 | 0.35 | 0.37 | 0.3 | 0.34 | 0.34 | 0.33 | 0.33 | 0.32 | 0.27
| PSZ-HEATCOOL:2_FAN | 0.76 | 0.78 | 0.81 | 0.75 | 0.72 | 0.75 | 0.84 | 0.72 | 0.8 | 0.75 | 0.73 | 0.8 | 0.74 | 0.78 | 0.75 | 0.68
| PSZ-HEATCOOL:3_FAN | 0.08 | 0.08 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.07 | 0.06
| PSZ-HEATCOOL:4_FAN | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.45 | 0.43 | 0.43 | 0.43 | 0.43
| PSZ-HEATCOOL:5_FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.04
| PSZ-HEATCOOL:6_FAN | 0.32 | 0.32 | 0.32 | 0.32 | 0.3 | 0.32 | 0.29 | 0.31 | 0.36 | 0.3 | 0.31 | 0.36 | 0.31 | 0.34 | 0.31 | 0.29
| PSZ-HEATCOOL:7_FAN | 1.54 | 1.53 | 1.56 | 1.57 | 1.51 | 1.6 | 1.45 | 1.52 | 1.8 | 1.49 | 1.54 | 1.79 | 1.55 | 1.7 | 1.55 | 1.46
| PSZ-HEATCOOL:8_FAN | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12 | 0.11 | 0.12 | 0.14 | 0.11 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.11
| PSZ-HEATCOOL:9_FAN | 0.37 | 0.37 | 0.35 | 0.34 | 0.31 | 0.32 | 0.25 | 0.32 | 0.34 | 0.27 | 0.32 | 0.34 | 0.32 | 0.32 | 0.29 | 0.23
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.07845 | 0.10762 | 0.089033 | 0.10101 | 0.12307 | 0.094576 | 0.14496 | 0.068552 | 0.037255 | 0.071466 | 0.098348 | 0.037265 | 0.05456 | 0.071094 | 0.054757 | 0.091282
| Total Cost ($/m2) | 14.22 | 18.02 | 15.05 | 15.58 | 17.95 | 14.83 | 19.98 | 10.16 | 5.46 | 9.59 | 14.32 | 5.3 | 8.11 | 9.98 | 7.94 | 14.14
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011459 | 0.0081727 | 0.0085306 | 0.010543 | 0.0084202 | 0.0080577 | 0.0084259 | 0.0099716 | 0.0071361 | 0.0083129 | 0.0087349 | 0.0071306 | 0.0079411 | 0.00857 | 0.0079388 | 0.0041676
| Total Cost ($/m2) | 1.27 | 1.21 | 1.15 | 1.92 | 1.25 | 1.26 | 1.59 | 2.27 | 1.41 | 1.87 | 2.35 | 1.68 | 2.49 | 2.45 | 2.9 | 2.11
Total Utility Costs
| Cost Intensity ($/m2) | 15.48 | 19.23 | 16.2 | 17.5 | 19.2 | 16.09 | 21.57 | 12.43 | 6.87 | 11.46 | 16.68 | 6.99 | 10.6 | 12.42 | 10.84 | 16.25
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 1894.4444 | 236.1111 | 2527.7778 | 0 | 169.4444 | 66.6667 | 6552.7778 | 1522.2222 | 1500 | 15277.7778 | 7819.4444 | 33308.3333 | 21052.7778 | 44769.4444 | 105275
| Cooling | 226927.7778 | 172797.2222 | 178319.4444 | 122322.2222 | 94911.1111 | 132911.1111 | 65630.5556 | 98127.7778 | 89794.4444 | 51494.4444 | 80105.5556 | 68583.3333 | 73919.4444 | 51027.7778 | 49816.6667 | 34233.3333
| Interior Lighting | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889 | 174538.8889
| Exterior Lighting | 32950 | 32891.6667 | 32883.3333 | 32938.8889 | 32933.3333 | 32900 | 32863.8889 | 32897.2222 | 32891.6667 | 32844.4444 | 32852.7778 | 32858.3333 | 32880.5556 | 32838.8889 | 32830.5556 | 32633.3333
| Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 66786.1111 | 63622.2222 | 66594.4444 | 60619.4444 | 56950 | 62583.3333 | 54005.5556 | 56497.2222 | 63605.5556 | 52372.2222 | 55725 | 61272.2222 | 56063.8889 | 57608.3333 | 53847.2222 | 49119.4444
| Pumps | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 727294.4444 | 671838.8889 | 678666.6667 | 619038.8889 | 585422.2222 | 629194.4444 | 553197.2222 | 594705.5556 | 588444.4444 | 538841.6667 | 584588.8889 | 571163.8889 | 596800 | 563161.1111 | 581894.4444 | 621891.6667
Gas (MJ)
| Heating | 7610 | 109320 | 82690 | 195030 | 71570 | 134910 | 189700 | 341720 | 227840 | 309960 | 475190 | 343500 | 623400 | 508190 | 783690 | 1289500
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 247270 | 297050 | 268450 | 344990 | 335660 | 302930 | 376690 | 382640 | 375520 | 402260 | 415710 | 413990 | 444290 | 449470 | 491410 | 548430
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 444360 | 595850 | 540620 | 729500 | 596710 | 627320 | 755860 | 913840 | 792840 | 901700 | 1080380 | 946970 | 1257170 | 1147130 | 1464570 | 2027410
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3062620 | 3014470 | 2983820 | 2958040 | 2704230 | 2892410 | 2747370 | 3054780 | 2911240 | 2841530 | 3184900 | 3003160 | 3405650 | 3174510 | 3559390 | 4266220
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 1.6992 | 0.21178 | 2.2673 | 0 | 0.15198 | 0.059797 | 5.8775 | 1.3654 | 1.3454 | 13.7034 | 7.0137 | 29.876 | 18.8833 | 40.1561 | 94.4267
| Cooling (elec) | 203.5435 | 154.9909 | 159.9441 | 109.7172 | 85.1308 | 119.215 | 58.8675 | 88.016 | 80.5414 | 46.1881 | 71.8509 | 61.516 | 66.3022 | 45.7695 | 44.6832 | 30.7057
| Interior Lighting (elec) | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531 | 156.5531
| Exterior Lighting (elec) | 29.5546 | 29.5023 | 29.4948 | 29.5446 | 29.5396 | 29.5097 | 29.4774 | 29.5072 | 29.5023 | 29.4599 | 29.4674 | 29.4724 | 29.4923 | 29.4549 | 29.4475 | 29.2706
| Interior Equipment (elec) | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675 | 202.3675
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 59.904 | 57.0661 | 59.7321 | 54.3728 | 51.0815 | 56.1343 | 48.4404 | 50.6753 | 57.0512 | 46.9754 | 49.9827 | 54.9583 | 50.2867 | 51.6719 | 48.2984 | 44.0578
| Pumps (elec) | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605 | 0.42605
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 652.3486 | 602.6076 | 608.7318 | 555.2485 | 525.096 | 564.3576 | 496.1917 | 533.4227 | 527.8068 | 483.3154 | 524.3485 | 512.3069 | 535.3013 | 505.1288 | 521.9317 | 557.8073
Gas (MJ/m2)
| Heating (gas) | 1.8961 | 27.2375 | 20.6025 | 48.5924 | 17.8319 | 33.6133 | 47.2644 | 85.1407 | 56.7671 | 77.2276 | 118.3953 | 85.5842 | 155.3223 | 126.6173 | 195.2591 | 321.2834
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096 | 47.2096
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 61.6082 | 74.011 | 66.8853 | 85.9555 | 83.6309 | 75.4761 | 93.8536 | 95.3361 | 93.5621 | 100.2245 | 103.5756 | 103.1471 | 110.6964 | 111.987 | 122.4365 | 136.6433
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 110.7138 | 148.4581 | 134.6974 | 181.7575 | 148.6724 | 156.299 | 188.3252 | 227.6864 | 197.5389 | 224.6617 | 269.1805 | 235.9409 | 313.2283 | 285.8115 | 364.9027 | 505.1363
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 763.0625 | 751.0658 | 743.4292 | 737.006 | 673.7684 | 720.6541 | 684.5169 | 761.1091 | 725.3456 | 707.9771 | 793.529 | 748.2478 | 848.5296 | 790.9403 | 886.8345 | 1062.9436
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 124.6128 | 117.7666 | 105.8863 | 103.6858 | 103.7877 | 98.7765 | 99.8788 | 106.1103 | 98.9278 | 95.66 | 115.4931 | 112.0504 | 127.9731 | 132.1267 | 131.4847 | 168.8783
| Feb | 127.541 | 110.6627 | 106.5859 | 105.6214 | 107.326 | 102.1988 | 103.9422 | 99.2677 | 101.2073 | 98.3569 | 104.0381 | 99.9281 | 123.0143 | 118.3974 | 132.1283 | 162.8354
| Mar | 127.0193 | 121.2078 | 122.1921 | 111.3101 | 103.7666 | 104.9989 | 101.3271 | 107.2209 | 103.0914 | 103.4942 | 102.1144 | 103.9978 | 101.3315 | 107.0084 | 112.0412 | 125.4281
| Apr | 129.9654 | 129.2228 | 122.7207 | 118.4419 | 109.5378 | 119.9907 | 105.2864 | 108.8623 | 111.8068 | 104.1864 | 104.838 | 108.021 | 108.7511 | 102.5713 | 99.4344 | 101.6386
| May | 135.9997 | 139.0163 | 140.1479 | 129.3534 | 112.492 | 126.1075 | 106.001 | 118.397 | 117.0363 | 107.9776 | 114.7314 | 115.4871 | 129.0578 | 107.6017 | 106.6902 | 100.9311
| Jun | 142.8086 | 136.5865 | 157.9448 | 131.3073 | 110.0855 | 146.7476 | 107.4208 | 132.7664 | 122.9367 | 110.2953 | 124.8539 | 118.3702 | 128.1819 | 118.5598 | 120.2125 | 108.2105
| Jul | 138.3714 | 142.4561 | 155.3112 | 139.7339 | 117.4158 | 144.7472 | 122.324 | 139.7121 | 129.334 | 115.7926 | 131.9037 | 124.479 | 133.3217 | 118.6099 | 126.5211 | 109.4506
| Aug | 138.5665 | 147.2149 | 157.4236 | 132.5721 | 119.461 | 141.0174 | 107.2274 | 139.6047 | 128.2982 | 116.4081 | 136.5311 | 121.7585 | 133.2554 | 119.3863 | 126.6923 | 105.864
| Sep | 136.4829 | 138.023 | 145.4244 | 126.5618 | 117.0194 | 130.5579 | 116.932 | 120.997 | 119.2162 | 120.3159 | 118.4515 | 116.1401 | 115.6864 | 116.5718 | 112.1642 | 99.8858
| Oct | 135.9922 | 128.9657 | 125.6662 | 118.2343 | 109.7317 | 116.812 | 106.9797 | 116.3912 | 110.9709 | 104.4536 | 109.4076 | 109.3282 | 110.7377 | 104.4333 | 107.0584 | 110.9127
| Nov | 126.6991 | 124.1325 | 109.6782 | 108.9818 | 106.4231 | 104.323 | 103.4185 | 111.5585 | 102.3679 | 102.2682 | 109.249 | 101.9172 | 100.5025 | 102.6255 | 114.3294 | 130.7895
| Dec | 124.3119 | 124.4337 | 105.3982 | 107.2695 | 103.862 | 100.54 | 100.3676 | 101.135 | 97.9028 | 95.8909 | 110.9716 | 109.3385 | 129.5096 | 125.5131 | 130.2289 | 149.7648
Time of Peak Electrical Demand
| Jan | 22-JAN-08:00 | 22-JAN-08:00 | 29-JAN-20:15 | 24-JAN-20:00 | 26-JAN-20:15 | 18-JAN-20:30 | 16-JAN-08:00 | 31-JAN-07:15 | 26-JAN-20:30 | 29-JAN-08:00 | 08-JAN-08:15 | 06-JAN-07:15 | 06-JAN-07:15 | 07-JAN-08:15 | 09-JAN-07:15 | 13-JAN-08:00
| Feb | 25-FEB-08:00 | 20-FEB-20:30 | 28-FEB-20:15 | 20-FEB-20:30 | 12-FEB-08:00 | 27-FEB-20:15 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:30 | 21-FEB-20:30 | 11-FEB-08:15 | 12-FEB-20:00 | 04-FEB-08:15 | 26-FEB-08:15 | 02-FEB-07:15 | 04-FEB-08:15
| Mar | 05-MAR-08:00 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 31-MAR-19:30 | 30-MAR-19:15 | 30-MAR-19:30 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 31-MAR-19:30 | 26-MAR-19:15 | 19-MAR-19:00 | 04-MAR-08:15 | 04-MAR-08:15 | 14-MAR-06:15
| Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 05-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 29-APR-07:00 | 25-APR-19:30 | 02-APR-19:30 | 30-APR-19:30 | 15-APR-19:15 | 09-APR-07:15
| May | 20-MAY-07:00 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 28-MAY-07:00 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 28-MAY-07:00 | 29-MAY-07:00
| Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 17-JUN-07:00 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-07:00 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 24-JUN-07:00
| Jul | 29-JUL-07:00 | 03-JUL-19:30 | 11-JUL-19:45 | 02-JUL-19:00 | 09-JUL-07:00 | 24-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 13-JUL-19:30 | 17-JUL-19:30 | 13-JUL-19:00 | 22-JUL-07:00 | 08-JUL-07:00 | 29-JUL-19:00
| Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 13-AUG-07:00 | 04-AUG-19:15 | 27-AUG-19:15 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 25-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 13-AUG-07:00
| Sep | 02-SEP-07:00 | 16-SEP-07:00 | 09-SEP-19:15 | 10-SEP-19:15 | 09-SEP-07:00 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:15 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 04-SEP-07:00
| Oct | 07-OCT-07:00 | 29-OCT-19:15 | 02-OCT-19:15 | 21-OCT-19:15 | 07-OCT-07:00 | 03-OCT-19:15 | 16-OCT-19:15 | 20-OCT-19:15 | 01-OCT-19:15 | 09-OCT-19:15 | 31-OCT-19:15 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
| Nov | 01-NOV-19:15 | 26-NOV-08:00 | 05-NOV-19:15 | 23-NOV-08:00 | 12-NOV-08:00 | 11-NOV-08:00 | 11-NOV-08:00 | 04-NOV-07:00 | 09-NOV-20:00 | 04-NOV-19:15 | 02-NOV-19:30 | 12-NOV-08:00 | 30-NOV-07:15 | 04-NOV-07:15 | 25-NOV-08:15 | 23-NOV-08:15
| Dec | 16-DEC-08:00 | 03-DEC-08:00 | 13-DEC-20:30 | 31-DEC-08:00 | 18-DEC-20:15 | 09-DEC-08:00 | 17-DEC-08:00 | 21-DEC-07:15 | 08-DEC-20:30 | 31-DEC-20:00 | 31-DEC-08:15 | 12-DEC-07:15 | 31-DEC-08:15 | 11-DEC-07:15 | 31-DEC-08:15 | 29-DEC-08:00
Source Energy
| Total Source Energy (GJ) | 9170.01 | 9435.08 | 8318.19 | 8293.41 | 7174.38 | 8787.28 | 6989.13 | 8653.9 | 7894.65 | 4363.84 | 8642.4 | 7856.52 | 8757.16 | 8299.83 | 8799.21 | 10210.97
| Total Source Energy (MJ/m2) | 2284.74 | 2350.79 | 2072.51 | 2066.33 | 1787.52 | 2189.38 | 1741.37 | 2156.15 | 1966.98 | 1087.27 | 2153.29 | 1957.48 | 2181.88 | 2067.93 | 2192.35 | 2544.1
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
| Total Building | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13 | 2216.13
Emissions
| Carbon Equivalent (kg) | 207473.4546 | 234843.6169 | 214621.4974 | 203841.3554 | 79176.1141 | 223523.5981 | 78280.1755 | 176963.2218 | 254675.8933 | 55506.1246 | 331155.4422 | 250395.4063 | 226950.7074 | 226485.7134 | 225588.5091 | 211552.2339
| CO2 (kg) | 485012.4908 | 593371.9644 | 509964.9702 | 470788.9817 | 213747.2938 | 535308.427 | 211984.8261 | 407502.3659 | 601413.0037 | 140206.7292 | 775402.5223 | 592992.9794 | 536445.5337 | 538429.1841 | 535488.5941 | 543987.3185
| NOX (kg) | 835.5595 | 767.3127 | 839.8893 | 870.2071 | 184.5391 | 853.9412 | 183.4628 | 762.793 | 1020.2289 | 192.444 | 1360.535 | 998.6569 | 918.8565 | 903.9327 | 907.2019 | 645.0769
| SO2 (kg) | 3113.2332 | 3204.8255 | 2729.1972 | 2173.0203 | 1703.6656 | 3461.2379 | 1609.9424 | 2171.1532 | 2569.8364 | 416.7233 | 3939.9537 | 2494.4087 | 1408.8811 | 1504.0122 | 1373.7557 | 3166.2233
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0142 | 0.0091 | 0.0075 | 0.008 | 0.0008 | 0.0066 | 0.0008 | 0.0088 | 0.0101 | 0.0017 | 0.012 | 0.0098 | 0.0104 | 0.0105 | 0.0102 | 0.0109
| Water for Electricity (m3) | 385.2904 | 1093.16 | 20159.4 | 3865.03 | 10278.7 | 17261.3 | 9712.92 | 135.0202 | 2672.01 | 5505.24 | 906.9553 | 2593.54 | 925.8999 | 35672.9 | 902.7739 | 635.3748

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 8.82 | 53.11 | 2769.31
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2 | 9.01
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.28 | 0.28 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.2 | 0.35 | 0.35 | 0.35 | 0.5 | 0.5 | 0.58 | 0.65 | 0.65 | 9.87 | 59.52 | 3103.54
|  |  | Sat, Sun, Hol | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.5 | 0.34 | 0.34 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.34 | 0.35 | 0.65 | 0.65 | 0.5 | 0.5 | 0.5 | 10.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Laundry Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Laundry Water Equipment Temp Sched | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600